## 01_README
Qualitrol BOQ Matching Data Package - README
This workbook turns the earlier Qualitrol industry/application mapping into an explainable AI + rules-driven BOQ matching data model.
Section | Purpose | Recommended Use | Owner / Notes
Workbook Purpose | A structured data package for AI-assisted Qualitrol opportunity extraction, product matching, and BOQ generation. | Use this workbook as the controlled reference layer for the AI workflow. | All sheets are in English; rows with 'TBD' or blank cells should be completed by product/application engineers.
Recommended Workflow | Input documents are parsed, evidence is extracted, scenarios are mapped, requirements are structured, drawings are converted into asset lists, products are matched, quantities are calculated, and a draft BOQ is generated. | Do not let the AI generate a final BOQ directly from documents without evidence, rules, and review. | Human review should remain mandatory before quotation.
Scenario Master | Normalizes application scenarios into IDs, asset types, metrics, synonyms, product families, and quantity logic. | Use Scenario ID as the anchor across all downstream tables. | Start here when adding new application scenarios.
Metric Dictionary | Normalizes raw parameter names from customer documents into controlled metric names and units. | Map customer text to Standard Metric Name and Metric ID before product matching. | Prevents duplicate metrics such as 'oil temp', 'top oil temperature', and 'transformer oil temperature'.
Product Templates | Separates Product Master from Product Parameters. | Avoid wide columns such as Parameter 1/2/3; use one row per product-parameter combination. | Actual product models and validated capability values should be filled by product team.
Quantity Rules | Makes BOQ quantity calculation explainable. | Use drawing-derived asset counts plus Quantity Rule ID. | Each BOQ line should show Quantity Basis and Assumption.
AI Output Templates | Standard output tables for evidence, requirements, drawing asset list, matching results, draft BOQ, and missing information. | Use these as JSON/output schema targets in Dify, Power Automate, Python, or another orchestration layer. | Every result should include evidence, confidence, and review status.

## 02_Industry_Use_Cases (hidden)
Industry Use Cases - One Application Scenario Per Row
Use this sheet as a business-facing view. The technical matching workflow should use Scenario ID in the Scenario Master sheet.
Industry | Application Scenario | Qualitrol Products / Capabilities | Typical Metrics / Requirements | Target Customer Type | Potential Target Accounts | Notes
Transmission & Distribution Utilities | Main transformer online condition monitoring | Transformer monitoring; DGA; temperature monitoring; oil level/flow; pressure relief; asset software | Transformer count; oil temperature; winding temperature; dissolved gas composition; moisture in oil; load current; voltage level; SCADA protocol | National or regional grid operators; substation owners | State Grid; China Southern Power Grid; National Grid; TenneT; RTE; Terna; Hydro-Québec; BC Hydro; Powerlink; TransGrid | High priority because transformer failure risk and outage cost are high.
Transmission & Distribution Utilities | Bushing condition monitoring | Bushing monitoring; capacitance/tan delta monitoring; transformer monitoring platform | Capacitance change; tan delta / power factor; leakage current; phase comparison; voltage level; alarm threshold | Grid operators; transformer asset management teams | State Grid; China Southern Power Grid; AusNet; Duke Energy; AEP; Dominion Energy | Usually linked to high-voltage transformer fleets.
Transmission & Distribution Utilities | Circuit breaker health monitoring | Breaker monitoring; trip/close coil monitoring; mechanism timing; SF6 / pressure monitoring where applicable | Breaker count; operating time; trip/close timing; coil current; operations counter; SF6 pressure/density; voltage level | Substation operations; switchgear maintenance teams | State Grid; China Southern Power Grid; National Grid; TenneT; Duke Energy; Southern Company | Quantity normally depends on number of monitored breakers.
Transmission & Distribution Utilities | GIS partial discharge monitoring | GIS monitoring; partial discharge monitoring; UHF sensors; monitoring software | GIS bay count; voltage level; PD magnitude; UHF signal; monitoring zones; alarm thresholds; sensor location | GIS substation owners; high-voltage asset teams | State Grid; China Southern Power Grid; National Grid; TenneT; RTE; Terna | Requires drawing or GIS bay layout for quantity.
Transmission & Distribution Utilities | Grid disturbance and fault recording | Digital fault recorder; disturbance recorder; PMU; fault location; power quality recorder | Voltage/current channels; sampling rate; trigger logic; event timestamp accuracy; time sync; IEC/IEEE standard; station count | Protection, control, dispatch, and grid performance teams | State Grid; China Southern Power Grid; National Grid; AEMO-connected networks; Hydro-Québec | Often driven by grid code, disturbance analysis, or regulatory requirements.
Power Generation - Thermal / Gas / CCGT | Generator insulation monitoring | Iris Power generator PD monitoring; generator condition monitoring | Generator count; rated MW/MVA; voltage level; PD level; stator winding condition; online/offline mode; alarm thresholds | Power plant owners; generator maintenance teams | China Energy; Huaneng; Huadian; Datang; SPIC; Duke Energy; Entergy; AES; Engie | High value for large rotating machines.
Power Generation - Thermal / Gas / CCGT | Generator end-winding vibration monitoring | End-winding vibration monitoring; generator monitoring platform | Vibration amplitude; frequency; sensor count; winding location; generator speed; alarm thresholds | Power plant reliability teams | China Energy; Huaneng; Huadian; Datang; Origin Energy; AGL; Delta Electricity | Requires engineering review for sensor placement.
Power Generation - Hydro / Pumped Storage | Hydro generator air gap and rotor monitoring | Air gap monitoring; rotor flux monitoring; generator monitoring software | Air gap; rotor flux; eccentricity; speed; pole count; unit count; alarm thresholds | Hydropower operators; pumped storage operators | Three Gorges; State Grid Xinyuan; Huaneng Hydropower; Hydro-Québec; BC Hydro; Snowy Hydro; Statkraft | Quantity depends on generator units and sensor layout.
Nuclear Power | Main transformer and critical electrical asset monitoring | Transformer monitoring; DGA; generator monitoring; motor monitoring; breaker monitoring; power quality | Asset criticality; safety class if applicable; temperature; DGA gases; breaker timing; motor temperature; redundancy requirement | Nuclear plant operators and EPCs | CGN; CNNC; EDF; Ontario Power Generation; KHNP | Requires strict review and qualification documentation.
Renewable Energy / ESS | Renewable plant grid connection power quality monitoring | Power quality recorder; disturbance recorder; PMU; transformer monitoring | PCC count; voltage level; Class A PQ; harmonics; flicker; frequency; voltage ride-through; timestamp accuracy | Wind/solar/ESS operators; grid connection teams | SPIC New Energy; China Three Gorges Renewables; Longyuan; NextEra; Iberdrola; Enel Green Power; Ørsted; Vattenfall | Often linked to grid code compliance.
Renewable Energy / ESS | Step-up transformer monitoring | Transformer monitoring; DGA; temperature monitoring; bushing monitoring | Transformer count; oil temperature; winding temperature; DGA gases; moisture; load; ambient conditions | Renewable plant owners and EPCs | Goldwind project customers; Mingyang project customers; Sungrow project customers; NextEra; Iberdrola; Enel Green Power | Quantity usually one per monitored step-up transformer.
Data Centers | Critical power chain monitoring | Dry-type transformer monitoring; temperature monitoring; partial discharge monitoring; breaker monitoring; power quality | Transformer count; UPS/PCC count; temperature; humidity; harmonics; sags/swells; event logging; redundancy topology | Cloud providers; colocation data center operators | AWS; Microsoft; Google; Meta; Equinix; Digital Realty; GDS; Chindata; VNET; Alibaba Cloud; Tencent Cloud | Power quality and reliability requirements are strong.
Steel / Metallurgy | Plant power quality and disturbance monitoring | Power quality recorder; digital fault recorder; transformer monitoring; motor monitoring | Harmonics; flicker; voltage sag/swell; transient events; sampling rate; transformer load; motor current | Steel plants; smelters; electrical maintenance teams | Baowu; Ansteel; Shougang; HBIS; Shagang; ArcelorMittal; POSCO; Nippon Steel; JFE; BlueScope | Power disturbances can cause production losses.
Aluminium / Non-ferrous Metals | Rectifier transformer and high-energy process monitoring | Transformer monitoring; DGA; power quality recorder; DFR; motor monitoring | Rectifier transformer count; load current; harmonics; temperature; DGA gases; PQ Class; event recording | Aluminium smelters; copper/zinc/nickel operations | Chinalco; Hongqiao; Weiqiao; Alcoa; Tomago Aluminium; Portland Aluminium; Rio Tinto Aluminium | High-value use case with public references in similar applications.
Mining / Mineral Processing | Mine substation and large motor monitoring | Transformer monitoring; motor monitoring; breaker monitoring; power quality | Substation count; transformer count; motor count; voltage level; motor temperature; current; vibration; PQ events | Mining groups; concentrators; mineral processing plants | Zijin Mining; CMOC; China Minmetals; Jiangxi Copper; BHP; Rio Tinto; Fortescue; Vale; Glencore; Anglo American; Newmont | Often needs rugged environment requirements.
Oil & Gas / LNG / Petrochemical | Refinery or LNG plant electrical asset monitoring | Transformer monitoring; DGA; motor monitoring; breaker monitoring; partial discharge; power quality | Critical motor count; compressor motor ratings; transformer count; temperature; humidity; hazardous area requirements; SCADA protocol | Refineries; LNG operators; petrochemical plants | CNPC; Sinopec; CNOOC; Hengli; Rongsheng; Wanhua; Shell; BP; ExxonMobil; Chevron; TotalEnergies; Petronas; Aramco | Integration and hazardous-area constraints may require clarification.
Rail / Metro / Transportation | Traction substation monitoring | Transformer monitoring; breaker monitoring; power quality; DFR; partial discharge | Traction transformer count; rectifier transformer count; breaker count; voltage level; harmonics; feeder count | Rail operators; metro companies; traction power teams | China Railway; Shanghai Metro; Beijing Metro; Guangzhou Metro; Shenzhen Metro; MTR; Deutsche Bahn; JR East; Network Rail; SNCF | Quantity depends on traction substations, feeders, and breakers.
Water / Wastewater | Pump station motor and transformer monitoring | Motor monitoring; transformer monitoring; breaker monitoring; power quality | Pump motor count; motor rating; transformer count; operating temperature; current; vibration; PQ events | Water utilities; wastewater plant operators | Beijing Enterprises Water; Capital Eco-Pro; Guangdong Water; Veolia; Suez; Thames Water; Sydney Water | Good fit where pump availability is critical.
Airports / Ports / Large Campuses | High-reliability distribution monitoring | Transformer monitoring; breaker monitoring; power quality recorder; DFR | Substation count; feeder count; transformer count; breaker count; sags/swells; event timestamp; redundancy requirement | Airport groups; port operators; industrial parks | Shanghai Airport; Capital Airport; Guangzhou Baiyun Airport; Shenzhen Airport; SIPG; Ningbo-Zhoushan Port; PSA; DP World; Changi Airport Group | Often tied to resilience and operational continuity.
Semiconductor / Electronics Manufacturing | Power quality monitoring for sensitive manufacturing | Power quality recorder; disturbance recorder; transformer monitoring; breaker monitoring | Voltage sag duration; harmonics; flicker; transient events; Class A requirement; PCC count; feeder count | Semiconductor fabs; display fabs; precision manufacturers | TSMC; Samsung Semiconductor; SK hynix; SMIC; Hua Hong; YMTC; CXMT; BOE; TCL CSOT; Foxconn; Luxshare | Power quality events may impact yield.
Electrical Equipment OEM | Monitoring package integration into transformers and switchgear | Sensors; temperature; pressure relief; liquid level/flow; Buchholz relay; DGA; PD; bushing monitoring | OEM asset type; factory acceptance requirement; communication protocol; accessory count; enclosure rating; operating environment | Transformer OEMs; switchgear OEMs; GIS OEMs | TBEA; XD Group; Pinggao; Sieyuan; Taikai; Baoding Tianwei; Chint; XJ Electric; Siemens Energy; Hitachi Energy; GE Vernova; Schneider Electric; Eaton; Mitsubishi Electric | Can be bundled into OEM equipment offerings.
EPC / Design Institutes / Service Integrators | Monitoring solution packaged into new build or retrofit projects | Full monitoring system; software; sensors; DGA; PD; DFR; PQ; integration services | Project scope; asset count; I/O points; communication protocol; integration boundary; acceptance criteria | Power EPCs; design institutes; system integrators | POWERCHINA; Energy China; regional design institutes; Black & Veatch; Burns & McDonnell; Worley; Jacobs; Bechtel; Fluor | Important channel for early specification influence.

## 03_Scenario_Master
Scenario Master - Controlled Scenario Taxonomy
Use Scenario ID as the stable key for AI extraction, product matching, quantity rules, and BOQ generation.
Scenario ID | Scenario Category | Application Scenario | Asset Type | Typical Metrics / Requirements | Common Evidence Keywords / Synonyms | Related Product Families | Quantity Basis | Drawing Dependency | Requirement Output Fields | Review Notes
TR_DGA_001 | Transformer | Transformer dissolved gas monitoring | Oil-filled power transformer | DGA gas count; H2; CO; CO2; CH4; C2H2; C2H4; C2H6; O2/N2; moisture in oil; oil temperature | DGA; dissolved gas; gas-in-oil; online gas monitor; transformer oil analysis; hydrogen monitor; acetylene; oil chromatograph | DGA Monitor; Transformer Monitor; Asset Monitoring Software | 1 unit per monitored oil-filled transformer | Asset count from SLD or transformer list recommended | asset_tag; transformer_count; gas_count; oil_type; communication_protocol; alarm_threshold | Exclude dry-type transformers unless another non-DGA monitoring need exists.
TR_TEMP_001 | Transformer | Transformer oil and winding temperature monitoring | Power transformer / distribution transformer | Top oil temperature; winding temperature; hot-spot temperature; ambient temperature; cooling stage; load current | oil temp; winding temp; hot spot; temperature indicator; thermal monitor; cooling control; fan control | Transformer Temperature Monitor; Cooling Control; Transformer Monitor | 1 monitor per transformer or per transformer control cabinet | Asset count required; drawing useful but not mandatory | asset_tag; temperature_points; cooling_stage; ambient_range; alarm_setpoints | Confirm whether winding temperature is simulated, direct fiber, or RTD-based.
TR_BUSH_001 | Transformer | Transformer bushing condition monitoring | Transformer bushing | Capacitance; tan delta / power factor; leakage current; phase angle; voltage level; bushing count | bushing monitor; tan delta; capacitance; power factor; leakage current; high-voltage bushing | Bushing Monitor; Transformer Monitor; Asset Monitoring Software | Typically one monitoring set per transformer; channel count depends on bushing/phase count | Drawing or bushing list required for accurate channel count | asset_tag; bushing_count; phase_count; voltage_level; reference_voltage; alarm_threshold | Quantity may depend on three-phase/six-bushing configuration.
TR_PD_001 | Transformer | Transformer partial discharge monitoring | Power transformer | PD magnitude; PD location; UHF/HFCT/acoustic sensor count; voltage level; alarm threshold | partial discharge; PD; UHF; HFCT; acoustic; insulation defect; discharge monitoring | Partial Discharge Monitor; Transformer Monitor; PD Sensors | Sensor and monitor count depends on transformer design and monitoring zones | Drawing/engineering review recommended | asset_tag; sensor_type; sensor_count; voltage_level; monitoring_zone; alarm_threshold | Requires product engineer review for sensor placement.
TR_AUX_001 | Transformer | Transformer auxiliary protection and indication | Oil-filled transformer | Pressure relief; oil level; oil flow; Buchholz relay; temperature contacts; alarm/trip contacts | pressure relief; PRD; oil level; oil flow; Buchholz; relay; sudden pressure; alarm contacts | Sensors; Pressure Relief Device; Oil Level Indicator; Flow Indicator; Buchholz Relay | Quantity depends on transformer accessories and protection points | Asset accessory list required | asset_tag; accessory_type; contact_type; mounting; alarm_or_trip | Often OEM or replacement accessory opportunity.
DRY_TR_TEMP_001 | Transformer | Dry-type transformer temperature monitoring | Dry-type transformer | Winding temperature; ambient temperature; fan control; alarm/trip contacts; enclosure temperature | dry transformer; cast resin; winding temperature; fan control; temperature relay | Dry-Type Transformer Temperature Monitor | 1 monitor per dry-type transformer | Asset count required | asset_tag; winding_temperature_points; fan_control; alarm_contacts; ambient_range | DGA is not applicable to dry-type transformer.
BRK_HEALTH_001 | Breaker | Circuit breaker health monitoring | High-voltage / medium-voltage circuit breaker | Trip time; close time; coil current; operation count; contact wear; SF6 pressure/density; motor current | breaker monitor; trip coil; close coil; operating time; mechanism timing; SF6 density; CBM; circuit breaker diagnostics | Breaker Monitor; Switchgear Monitor; Asset Monitoring Software | 1 monitor per breaker; channel count depends on auxiliary contacts and mechanism points | Breaker count from SLD or switchgear list required | asset_tag; breaker_count; voltage_level; operating_mechanism; coil_voltage; sf6_required | Confirm breaker type and whether SF6 measurements are needed.
GIS_PD_001 | GIS | GIS partial discharge monitoring | Gas-insulated switchgear / GIS bay | PD signal; UHF sensor count; bay count; compartment count; voltage level; monitoring zone | GIS PD; UHF; gas insulated switchgear; GIS bay; partial discharge; switchgear insulation | GIS PD Monitor; UHF Sensor; PD Monitoring Software | Quantity based on GIS bay count, compartments, or monitoring zones | GIS layout/drawing strongly required | gis_bay_count; compartments; sensor_count; voltage_level; monitoring_zone; alarm_threshold | Avoid estimating sensor count without layout.
SWG_PD_001 | Switchgear | MV switchgear partial discharge monitoring | Medium-voltage switchgear / cable termination | PD level; HFCT/TEV/UHF sensor type; feeder count; cable termination count; voltage level | MV PD; switchgear PD; TEV; HFCT; cable termination; feeder insulation | Partial Discharge Monitor; Switchgear PD Sensors | Quantity based on switchgear panels/feeders/monitoring zones | Switchgear lineup drawing required for accuracy | panel_count; feeder_count; sensor_type; voltage_level; monitoring_zone | Panel-level or feeder-level scope must be confirmed.
GEN_PD_001 | Generator | Generator stator partial discharge monitoring | Generator | PD level; generator voltage; MW/MVA rating; stator winding; coupler count; online/offline mode | generator PD; stator PD; Iris Power; winding insulation; coupler; rotating machine PD | Generator PD Monitor; Iris Power Sensors; Generator Monitoring Software | Typically per generator unit; sensor/coupler count depends on generator design | Generator list required; design review recommended | generator_tag; voltage_level; rating_mva; sensor_count; online_mode; alarm_threshold | Large rotating machine expertise required.
GEN_EWV_001 | Generator | Generator end-winding vibration monitoring | Turbine generator / large generator | End-winding vibration; acceleration; frequency; sensor count; location; alarm threshold | end winding vibration; EWV; stator end winding; vibration sensor; generator vibration | End-Winding Vibration Monitor; Generator Monitoring Platform | Per generator unit; sensor count based on winding locations | Engineering design required | generator_tag; sensor_count; vibration_threshold; mounting_location; speed | Not every generator requires this; scope driven by risk and asset criticality.
GEN_AIRGAP_001 | Generator | Hydro generator air gap and rotor flux monitoring | Hydro generator / pumped storage generator | Air gap; rotor flux; eccentricity; pole count; speed; sensor count | air gap; rotor flux; eccentricity; hydro generator; pole flux; rotor monitoring | Air Gap Monitor; Rotor Flux Monitor; Generator Monitoring Software | Per generator unit; sensor count depends on generator design | Generator design and unit count required | generator_tag; unit_count; pole_count; sensor_count; speed; alarm_threshold | Strong use case for hydro and pumped storage.
MTR_PD_001 | Motor | Large motor insulation monitoring | Large MV/HV motor | PD level; motor voltage; motor rating; stator insulation condition; coupler/sensor count | motor PD; stator insulation; Iris Power motor; MV motor; HV motor; coupler | Motor PD Monitor; Motor Monitoring Platform | Per monitored motor; sensors depend on motor design | Motor list required | motor_tag; rating_kw; voltage_level; sensor_count; online_mode | Prioritize critical motors such as compressors, pumps, fans, mills.
MTR_TEMP_001 | Motor | Large motor thermal and condition monitoring | Large motor | RTD temperature; bearing temperature; load current; operating hours; vibration if applicable | motor temperature; RTD; bearing temperature; winding temperature; motor monitor; reliability | Motor Monitor; Temperature Monitor; Asset Monitoring Software | Per monitored motor; channel count depends on RTD/bearing points | Motor list and I/O point list required | motor_tag; rtd_count; bearing_points; current; alarm_threshold | Clarify whether vibration is in scope or handled by another system.
PQ_CLASSA_001 | Grid / Power Quality | Class A power quality monitoring | PCC, bus, feeder, grid connection point | Class A compliance; harmonics; flicker; voltage sag/swell; frequency; unbalance; transient; sampling rate | Class A PQ; power quality; harmonics; flicker; sag; swell; EN 50160; IEC 61000; PQ recorder | Power Quality Recorder; Disturbance Recorder; Monitoring Software | Typically 1 unit per PCC/bus/monitored feeder | SLD strongly recommended to identify PCCs and feeders | pcc_count; voltage_level; current_channels; pq_class; standard; time_sync | Do not recommend non-Class A product when Class A is explicitly required.
DFR_DDR_001 | Grid / Disturbance | Digital fault and disturbance recording | Substation bus, feeder, generator connection, PCC | Voltage/current channels; sampling rate; trigger logic; event recording; time sync; sequence of events | DFR; DDR; disturbance recorder; fault recorder; transient recorder; event recorder; fault analysis | Digital Fault Recorder; Disturbance Recorder; Monitoring Software | 1 unit per station/bus or per channel group depending on scope | SLD and channel list required | channel_count; voltage_channels; current_channels; sampling_rate; trigger; time_sync | Channel count is the critical quantity driver.
PMU_001 | Grid / Synchrophasor | Phasor measurement and wide-area monitoring | Transmission grid, PCC, generator interconnection | Synchrophasor; timestamp accuracy; reporting rate; voltage/current channels; PTP/GPS time sync | PMU; synchrophasor; phasor measurement; wide-area monitoring; WAMS; IEEE C37.118 | PMU; Disturbance Recorder; Grid Monitoring Software | 1 unit per monitored bus/PCC/measurement point | SLD and grid measurement points required | measurement_point_count; reporting_rate; time_sync; standard; channel_count | Often driven by grid operator requirements.
FAULT_LOC_001 | Grid / Fault Location | Transmission line fault location | Transmission line / feeder | Line length; voltage level; current/voltage channels; fault type; GPS time sync | fault locator; line fault; distance to fault; travelling wave; transmission line | Fault Location System; DFR; Grid Monitoring Software; PF_TWS | Per line or monitored terminal depending on topology | Line diagram and terminal list required | line_count; terminal_count; voltage_level; time_sync; line_length | Quantity depends on single-ended or multi-ended solution.
SUB_SOFT_001 | Software / Platform | Substation or fleet asset monitoring software | Multi-asset substation / fleet | Asset count; data points; protocols; alarm rules; dashboards; historian/SCADA integration | asset management; monitoring software; dashboard; SCADA; Modbus; IEC 61850; DNP3; historian | Asset Monitoring Software; SmartSub / Monitoring Platform | Per site, per asset, or per software license model | Documented site scope and integration points required | site_count; asset_count; protocol; tag_count; user_count; license_model | License model must be confirmed with product/commercial team.
CAB_ENV_001 | Environment | Cabinet or substation environmental monitoring | Monitoring cabinet, control room, outdoor enclosure | Ambient temperature; humidity; enclosure rating; IP/NEMA rating; heater/fan; condensation | ambient temperature; humidity; RH; IP rating; enclosure; condensation; cabinet heater; outdoor environment | Environmental Sensors; Cabinet Accessories; Monitoring Platform | Per cabinet/enclosure or per monitoring zone | Cabinet count required | cabinet_count; ambient_range; humidity_range; enclosure_rating; power_supply | Useful as supporting requirements for product selection.
COMM_SCADA_001 | Integration | SCADA and communication integration | Monitoring system / site integration | Modbus; DNP3; IEC 61850; IEC 60870; Ethernet; fiber; serial; cybersecurity; time sync | SCADA; protocol; Modbus; DNP3; IEC 61850; Ethernet; integration; gateway; API | Gateway; Monitoring Software; Communication Module | Usually per site/system; module count depends on architecture | Integration architecture required | protocol; network_type; cybersecurity; time_sync; gateway_required | This scenario may not create a stand-alone BOQ line but affects product selection.
FMS_001 | Grid / Disturbance | Centralized fault management system and DFR data platform | Multi-DFR substation / substation network server | Server count; iQ+ license count; managed device count; communication network | FMS; fault management system; iQ+; iQ plus; master station; CASHEL FMS; centralized recording; central server; substation data server; DFR master station; iQ master station; data management platform; rackmount server; network server | PF_DFR; PF_TWS; PF_PMU; PF_SOFTWARE | 1 server system per site; additional client workstation licenses per operator | Network device inventory and site topology helpful | server_count; managed_device_count; site_count; client_count | Always paired with 2+ IDM+/TWS deployments. iQ+ Master Station is the standard software.
GIS_ARC_001 | GIS | GIS arc flash detection and localization | Gas-insulated switchgear / GIS compartment | Arc event count; arc location; gas compartment; UHF signal level; flashover | arc detection; arc flash; arc localization; GIS arc; flashover; GIS flashover; arc discharge; flashover detection; arc fault detection; arc event | PF_GIS_PD | No additional hardware; feature of PDMG-RH Gen3 (uses existing UHF sensors) | GIS layout and compartment list required for localization | gis_bay_count; arc_detection_option; compartment_list | Arc Detection is an add-on feature of PDMG-RH Gen3. No extra hardware needed. Only quote if PDMG-RH Gen3 is already in scope.
WAMS_001 | Grid / Synchrophasor | Wide area monitoring system for multi-site grid stability | Multi-substation transmission grid / phasor data concentrator | PMU count; phasor data concentrator count; reporting rate; GPS latency; site count | WAMS; wide area monitoring; wide area measurement system; PDC; phasor data concentrator; real-time oscillation monitoring; power swing monitoring; inter-area oscillation; grid stability monitoring; frequency monitoring; voltage angle | PF_PMU; PF_SOFTWARE | 1 PMU per monitored grid measurement point; 1 PDC per substation cluster | Grid topology and SLD required; multi-site coordination | pmu_count; site_count; grid_segment; reporting_rate | Typically integrated with GCCIA or national SCADA. PMU_001 is per-device; WAMS_001 covers the system-wide wide-area network use case.

## 04_Metric_Dictionary
Metric Dictionary - Standard Parameter Names and Units
Map customer raw terms to these standard metrics before product matching. This avoids uncontrolled AI-generated parameter names.
Metric ID | Standard Metric Name | Synonyms / Raw Terms | Standard Unit | Data Type | Applies To | Used For | Example Values | Required for Matching | Normalization Notes
MET_ASSET_COUNT | Asset Count | quantity; qty; number of assets; equipment count | count | integer | All assets | Quantity calculation | 2 transformers; 6 breakers | Yes | Usually extracted from drawing asset list or equipment list.
MET_ASSET_TAG | Asset Tag | tag; equipment ID; device name; transformer name; breaker ID | text | text | All assets | Evidence linking and BOQ basis | T1; T2; CB-101 | Yes | Preserve original tag exactly.
MET_ASSET_TYPE | Asset Type | equipment type; device type; asset class | text | controlled text | All assets | Scenario and product filtering | Transformer; GIS; Circuit Breaker | Yes | Map to controlled asset type values.
MET_VOLTAGE_LEVEL | Voltage Level | rated voltage; system voltage; nominal voltage; kV level | kV | number/range | Transformer; GIS; Breaker; Grid; Motor; Generator | Compatibility and engineering scope | 33 kV; 110 kV; 220 kV | Yes | Normalize all voltage values to kV.
MET_POWER_RATING | Power Rating | MVA; MW; kW; rated power; apparent power | MVA/MW/kW | number | Transformer; Generator; Motor | Sizing and priority | 100 MVA; 500 MW; 2 MW | Preferred | Keep original unit and normalized unit if possible.
MET_CURRENT_CHANNELS | Current Channels | CT inputs; current inputs; current channels | count | integer | DFR; PQ; PMU; Breaker | Channel count and product configuration | 4; 8; 16 | Yes for recorders | Count physical measurement channels.
MET_VOLTAGE_CHANNELS | Voltage Channels | VT inputs; voltage inputs; voltage channels | count | integer | DFR; PQ; PMU | Channel count and product configuration | 3; 4; 8 | Yes for recorders | Count physical measurement channels.
MET_PQ_CLASS | Power Quality Class | Class A; PQ class; IEC 61000-4-30 class | text | controlled text | Power Quality | Product eligibility | Class A; Class S | Yes when specified | If Class A is specified, lower class should be excluded.
MET_HARMONICS | Harmonics Requirement | THD; harmonic; interharmonic; harmonic measurement | % / order | text/number | Power Quality; Industrial | PQ product capability | up to 50th order; THD < 5% | Preferred | Keep both measurement range and limit if stated.
MET_FLICKER | Flicker Requirement | Pst; Plt; flicker | text/number | text/number | Power Quality | PQ product capability | Pst/Plt required | Preferred | Map to PQ capability.
MET_SAG_SWELL | Sag / Swell Recording | voltage sag; voltage dip; voltage swell; RMS variation | text | boolean/text | Power Quality; DFR | Event recording capability | required; threshold 90% | Preferred | If threshold is provided, retain it.
MET_SAMPLING_RATE | Sampling Rate | sample rate; sampling frequency; waveform sampling | samples/cycle or Hz | number/text | DFR; PQ; PMU | Recorder selection | 256 samples/cycle; 10 kHz | Preferred | Normalize carefully; retain original phrase.
MET_TIME_SYNC | Time Synchronization | GPS; IRIG-B; PTP; NTP; time sync; timestamp accuracy | text | controlled text | DFR; PQ; PMU; Grid Monitoring | System integration | GPS; IRIG-B; PTP | Preferred | Important for event correlation.
MET_REPORTING_RATE | Reporting Rate | PMU rate; frames per second; reporting frequency | fps / Hz | number | PMU | PMU compliance | 25 fps; 50 fps; 60 fps | Preferred | Normalize to frames per second if possible.
MET_DGA_GAS_COUNT | DGA Gas Count | number of gases; gas channels; 5-gas; 9-gas; multi-gas | count | integer | Transformer DGA | Product selection | 1; 5; 9 | Yes for DGA | Map 'multi-gas' to unknown unless exact count is given.
MET_DGA_GAS_SPECIES | DGA Gas Species | H2; CO; CO2; CH4; C2H2; C2H4; C2H6; O2; N2 | text | list | Transformer DGA | Product capability matching | H2, CO, C2H2 | Preferred | Extract individual gas names if provided.
MET_MOISTURE_OIL | Moisture in Oil | water in oil; moisture; ppm water; relative saturation | ppm / %RS | number | Transformer | Transformer condition monitoring | 10 ppm; 20% RS | Preferred | Keep ppm and relative saturation separate.
MET_OIL_TEMPERATURE | Oil Temperature | top oil temp; oil temp; transformer oil temperature | °C | number/range | Transformer | Temperature monitoring and DGA correction | 95°C; -20 to 70°C ambient | Preferred | Differentiate oil temperature from ambient temperature.
MET_WINDING_TEMP | Winding Temperature | winding temp; hot-spot; hotspot temperature | °C | number/range | Transformer; Motor; Generator | Thermal monitoring | 120°C | Preferred | Map transformer and motor contexts separately.
MET_AMBIENT_TEMP | Ambient Temperature | site temperature; operating temperature; environment temperature | °C | range | All equipment / Enclosure | Environmental suitability | -20 to 70°C | Preferred | Do not confuse with asset operating temperature.
MET_HUMIDITY | Humidity | RH; relative humidity; moisture; ambient humidity | %RH | range/number | Cabinet; Environment; Site | Environmental suitability | 95% RH non-condensing | Preferred | Retain condensation condition.
MET_ENCLOSURE_RATING | Enclosure Rating | IP rating; NEMA; outdoor enclosure; cabinet rating | text | controlled text | Cabinet; Monitoring Device | Hardware configuration | IP54; IP65; NEMA 4X | Preferred | Keep IP and NEMA as text.
MET_PROTOCOL | Communication Protocol | SCADA; Modbus; DNP3; IEC 61850; IEC 60870; protocol | text | list | All monitoring systems | Integration and product selection | Modbus TCP; DNP3; IEC 61850 | Yes if specified | Multiple protocols may be required.
MET_NETWORK | Network Interface | Ethernet; serial; RS485; fiber; wireless | text | list | All monitoring systems | Integration and accessory selection | Ethernet; RS485; fiber optic | Preferred | Useful for gateways and accessories.
MET_POWER_SUPPLY | Power Supply | auxiliary supply; control power; AC/DC supply | V AC/DC | text/number | All devices | Hardware configuration | 110 VDC; 220 VAC | Preferred | Retain AC/DC.
MET_CONTACT_TYPE | Contact Type | alarm contact; trip contact; relay contact; dry contact | text | controlled text | Sensors; Protection accessories | I/O configuration | NO/NC; alarm; trip | Preferred | Map to I/O requirements.
MET_ALARM_THRESHOLD | Alarm Threshold | alarm; warning; trip threshold; setpoint | varies | number/text | All monitoring | Configuration and acceptance | H2 alarm 100 ppm; temp alarm 95°C | Preferred | Attach threshold to the relevant metric.
MET_PD_LEVEL | Partial Discharge Level | PD magnitude; apparent charge; discharge level | pC / mV / dB | number/text | Transformer; GIS; Switchgear; Generator; Motor | PD monitoring requirement | 500 pC; warning level TBD | Preferred | Units vary by PD method; retain original unit.
MET_SENSOR_TYPE | Sensor Type | UHF; HFCT; TEV; acoustic; coupler; RTD | text | controlled text | PD; Temperature; Generator; Motor | Sensor selection | UHF; HFCT; RTD | Preferred | Map to product/sensor family.
MET_SENSOR_COUNT | Sensor Count | number of sensors; channels; couplers; probes | count | integer | All monitoring | Quantity and configuration | 3 sensors; 6 couplers | Yes when specified | May be calculated from asset count if not specified.
MET_BUSHING_COUNT | Bushing Count | number of bushings; HV bushings; phase bushings | count | integer | Transformer Bushing | Channel count and quantity | 3; 6 | Yes for bushing monitoring | Use bushing list/drawing for final quantity.
MET_CAPACITANCE | Bushing Capacitance | capacitance; C1; C2 | pF / nF | number | Transformer Bushing | Bushing monitoring | 500 pF | Preferred | May not be available in early-stage specs.
MET_TAN_DELTA | Tan Delta / Power Factor | tan delta; dielectric loss; power factor | % / decimal | number | Transformer Bushing | Bushing condition monitoring | 0.5%; 0.005 | Preferred | Normalize % vs decimal carefully.
MET_BREAKER_COUNT | Breaker Count | number of breakers; CB count; circuit breaker quantity | count | integer | Circuit Breaker | BOQ quantity | 6 breakers | Yes for breaker monitoring | Prefer SLD-derived count.
MET_TRIP_CLOSE_TIME | Trip / Close Time | opening time; closing time; trip time; close time | ms | number | Circuit Breaker | Breaker health monitoring | 40 ms; 60 ms | Preferred | May be an acceptance value or measured value.
MET_COIL_CURRENT | Coil Current | trip coil current; close coil current; coil signature | A | number | Circuit Breaker | Breaker mechanism diagnostics | 2.5 A | Preferred | Usually capability requirement rather than product filtering.
MET_SF6_PRESSURE | SF6 Pressure / Density | SF6; gas density; pressure; density relay | bar / MPa / density | number/text | GIS; Circuit Breaker | Gas monitoring scope | 0.5 MPa; density monitor required | Preferred | Only applicable to SF6 assets.
MET_GIS_BAY_COUNT | GIS Bay Count | bay count; GIS bays; compartments; feeders | count | integer | GIS | BOQ quantity | 8 bays | Yes for GIS PD | Prefer GIS layout.
MET_PANEL_COUNT | Switchgear Panel Count | switchgear panels; cubicles; feeders; cells | count | integer | MV Switchgear | BOQ quantity | 12 panels | Yes for switchgear PD | Panel vs feeder count must be distinguished.
MET_GENERATOR_COUNT | Generator Count | number of units; generator units; turbine units | count | integer | Generator | BOQ quantity | 4 units | Yes for generator monitoring | Extract unit number and tag.
MET_AIR_GAP | Air Gap | airgap; rotor-stator gap; eccentricity | mm / % | number | Hydro Generator | Air gap monitoring | 12 mm | Preferred | Often configuration/monitoring metric.
MET_ROTOR_FLUX | Rotor Flux | pole flux; flux probe; rotor flux | text/relative | number/text | Generator | Rotor monitoring | required; pole flux trend | Preferred | Exact units may vary by system.
MET_VIBRATION | Vibration | end winding vibration; bearing vibration; acceleration | mm/s / g / μm | number/text | Generator; Motor | Condition monitoring | 5 mm/s; 2 g | Preferred | Associate with location and axis if available.
MET_MOTOR_COUNT | Motor Count | number of motors; critical motors; pump motors; compressor motors | count | integer | Motor | BOQ quantity | 8 motors | Yes for motor monitoring | Use equipment list for final count.
MET_MOTOR_RTD_COUNT | Motor RTD Count | RTDs; temperature channels; winding RTDs; bearing RTDs | count | integer | Motor | Channel count | 6 winding RTDs; 2 bearing RTDs | Preferred | Required for temperature channel configuration.
MET_LICENSE_SCOPE | Software License Scope | site license; asset license; tag count; user count; software license | text/count | text/integer | Software | Commercial configuration | 100 tags; 5 users; site license | Preferred | Must be confirmed by product/commercial team.
MET_FEEDER_COUNT | Feeder / Circuit Count | feeder count; feeder; number of feeders; bay count; circuit count; number of circuits; feeders per panel; protected feeders; monitored feeders | count | integer | DFR; PQ; PMU; TWS | DFR model selection (determines analog channel count needed); TWS line module count | 6 feeders; 12 bays | Yes (for DFR/TWS sizing) | 1 feeder = typically 3 current + 1-3 voltage channels for full DFR coverage.
MET_LINE_COUNT | Transmission Line Count | line count; number of lines; transmission lines; monitored lines; line ends; circuits | count | integer | TWS; DFR | TWS FL module selection (FL-8 = 2/4/6/8 lines; FL-1 = 1 line) | 4 transmission lines; 2 line ends | Yes (for TWS) | TWS FL-8 starts with 2-line module, expandable to 8 in steps of 2.
MET_ANALOG_CHANNELS | Total Analog Channel Count | analog channels; AI count; analog inputs; channel count; total channels; number of analog; A/D channels; recording channels | count | integer | DFR; PQ; PMU; INFORMA PMD-A | IDM+ model/variant selection (9, 18, or 36 analog channels) | 9 analog channels; 18 AI; 36A | Yes (for DFR model selection) | IDM+ 9=9A/32D, IDM+ 18=18A/64D, IDM+ 36=36A/128D. Rule of thumb: 3 current + 3 voltage per feeder = 6 channels/feeder.
MET_DFR_FUNCTIONS | Required DFR / Recorder Functions | DFR functions; recording functions; monitoring options; PMU option; TWS option; Class A PQ option; SOE option; multifunctional recorder | text | controlled text (multi-select) | DFR; PMU; TWS | Determines which optional functions to order with IDM+: PMU, TWS card, Class A PQ | DFR + PMU; DFR + TWS + PMU; full functions | Yes (where stated) | IDM+ base = DFR+DDR. Options: +PMU (IEEE C37.118), +TWS card (±60m FL), +Class A PQ (IEC 61000-4-30 Class A).
MET_GPS_SYNC_ACCURACY | GPS Time Sync Accuracy | GPS accuracy; time tagging accuracy; timestamp accuracy; GPS time reference; time synchronization accuracy; 1PPS accuracy; IRIG-B accuracy | ns | number | TWS; PMU; DFR | Verify GPS accuracy meets double-ended TWS requirement (100 ns) and PMU C37.118 | 100 ns GPS; 1 µs IRIG-B | Yes (for TWS double-ended) | TWS double-ended requires GPS 100 ns. IDM+ GPS input provides 100 ns tagging.

## 05_Synonym_Mapping (hidden)
Synonym Mapping - Raw Customer Terms to Scenario and Metric IDs
This sheet can be expanded over time with real customer document expressions. It supports both keyword and semantic matching.
Raw Term / Phrase | Mapped Scenario ID | Mapped Metric ID | Mapped Standard Meaning | Asset Context | Mapping Priority | Notes
online oil gas analysis | TR_DGA_001 | MET_DGA_GAS_SPECIES | Transformer dissolved gas monitoring | Transformer | High | Strong DGA evidence.
oil chromatograph | TR_DGA_001 | MET_DGA_GAS_COUNT | DGA monitor requirement | Transformer | High | May imply multi-gas DGA.
hydrogen monitor | TR_DGA_001 | MET_DGA_GAS_SPECIES | Hydrogen gas monitoring in transformer oil | Transformer | Medium | Could be single-gas DGA; confirm gas count.
top oil temperature | TR_TEMP_001 | MET_OIL_TEMPERATURE | Transformer oil temperature | Transformer | High
hot spot temperature | TR_TEMP_001 | MET_WINDING_TEMP | Transformer winding hot-spot temperature | Transformer | High
bushing tan delta | TR_BUSH_001 | MET_TAN_DELTA | Transformer bushing condition monitoring | Transformer bushing | High
bushing capacitance | TR_BUSH_001 | MET_CAPACITANCE | Transformer bushing capacitance monitoring | Transformer bushing | High
breaker timing | BRK_HEALTH_001 | MET_TRIP_CLOSE_TIME | Circuit breaker mechanism timing | Circuit breaker | High
trip coil current | BRK_HEALTH_001 | MET_COIL_CURRENT | Breaker trip coil current signature | Circuit breaker | High
SF6 density | BRK_HEALTH_001 | MET_SF6_PRESSURE | Gas density/pressure monitoring | Circuit breaker / GIS | Medium | Check whether asset is breaker or GIS.
GIS UHF | GIS_PD_001 | MET_SENSOR_TYPE | GIS partial discharge monitoring | GIS | High
TEV sensor | SWG_PD_001 | MET_SENSOR_TYPE | MV switchgear PD sensor | Switchgear | Medium | May also appear in cable/switchgear PD scope.
HFCT | SWG_PD_001 | MET_SENSOR_TYPE | HFCT sensor for PD/current path monitoring | Switchgear / Cable / Transformer | Medium | Need asset context.
stator PD | GEN_PD_001 | MET_PD_LEVEL | Generator stator partial discharge monitoring | Generator | High
Iris Power | GEN_PD_001 | MET_PD_LEVEL | Generator or motor monitoring product clue | Generator / Motor | Medium | Use asset context to distinguish generator vs motor.
end winding vibration | GEN_EWV_001 | MET_VIBRATION | Generator end-winding vibration monitoring | Generator | High
air gap | GEN_AIRGAP_001 | MET_AIR_GAP | Hydro generator air gap monitoring | Hydro generator | High
rotor flux | GEN_AIRGAP_001 | MET_ROTOR_FLUX | Generator rotor flux monitoring | Generator | High
Class A PQ | PQ_CLASSA_001 | MET_PQ_CLASS | Class A power quality monitoring | Grid / PCC | High
harmonic analysis | PQ_CLASSA_001 | MET_HARMONICS | Power quality harmonics monitoring | Grid / Industrial | Medium | Confirm if recorder requirement or study only.
fault recorder | DFR_DDR_001 | MET_SAMPLING_RATE | Digital fault recording | Substation / Feeder | High
disturbance recorder | DFR_DDR_001 | MET_SAMPLING_RATE | Digital disturbance recording | Grid / Plant | High
PMU | PMU_001 | MET_REPORTING_RATE | Phasor measurement | Grid / PCC | High
synchrophasor | PMU_001 | MET_REPORTING_RATE | Synchrophasor measurement | Grid | High
Modbus TCP | COMM_SCADA_001 | MET_PROTOCOL | Communication protocol | All monitoring systems | High
IEC 61850 | COMM_SCADA_001 | MET_PROTOCOL | Substation communication protocol | Substation systems | High
IP65 | CAB_ENV_001 | MET_ENCLOSURE_RATING | Enclosure rating | Cabinet / outdoor device | Medium
95% RH | CAB_ENV_001 | MET_HUMIDITY | Operating humidity | Environment | Medium
TWS | FAULT_LOC_001 |  | Traveling Wave System (fault locator) | Transmission line | High | Abbreviation used in Qualitrol/Hathaway product line; word-boundary matched.
traveling wave system | FAULT_LOC_001 |  | Traveling wave fault location system | Transmission line | High | Full product category name.
travelling wave system | FAULT_LOC_001 |  | Travelling wave fault location system (UK sp.) | Transmission line | High | UK spelling variant.
traveling wave fault | FAULT_LOC_001 |  | Traveling wave fault location method | Transmission line | High | Common phrase in specifications.
travelling wave | FAULT_LOC_001 |  | Travelling wave fault location | Transmission line | Medium | Shorter form; may appear in protection specs.
fault locator | FAULT_LOC_001 |  | Transmission line fault locator device | Transmission line | High | Generic device name.
line fault location | FAULT_LOC_001 |  | Transmission line fault location | Transmission line | High | Common spec phrase.
distance to fault | FAULT_LOC_001 |  | Fault distance measurement on transmission line | Transmission line | High | Measurement output of fault locator.
TWS FL | FAULT_LOC_001 |  | Qualitrol TWS FL-series product reference | Transmission line | High | Matches TWS FL-2 and other FL models.
TWFL | FAULT_LOC_001 |  | Traveling Wave Fault Locator acronym | Transmission line | High | Acronym form.
transmission line fault | FAULT_LOC_001 |  | Fault on transmission line | Transmission line | Medium | May appear in protection relay specs.
single-ended fault location | FAULT_LOC_001 |  | Single-ended traveling wave fault location | Transmission line | High | Single-end TWS method.
double-ended fault location | FAULT_LOC_001 |  | Double-ended traveling wave fault location | Transmission line | High | Double-end GPS-sync TWS method.
IDM+ | DFR_DDR_001; PMU_001; FAULT_LOC_001; PQ_CLASSA_001 | MET_SAMPLING_RATE | Qualitrol IDM+ multifunction recorder (DFR/DDR/PMU/TWS/PQ) | Substation / feeder | High
IDM plus | DFR_DDR_001 |  | Qualitrol IDM+ multifunction recorder | Substation / feeder | High
IDM | DFR_DDR_001 | MET_SAMPLING_RATE | Qualitrol IDM/IDM+ fault recorder (legacy or current) | Substation | Medium
Hathaway DFR | DFR_DDR_001 |  | Hathaway (Qualitrol) digital fault recorder | Substation | High
Hathaway IDM | DFR_DDR_001; PMU_001 |  | Hathaway IDM fault and disturbance recorder with PMU option | Substation / grid | High
DDR | DFR_DDR_001 | MET_SAMPLING_RATE | Dynamic Disturbance Recorder (long-duration slow scan recording) | Substation / grid | High
dynamic disturbance recorder | DFR_DDR_001 |  | Long-duration slow scan recording of power system disturbances | Grid | High
CFR | DFR_DDR_001 |  | Continuous Fault Recorder (continuous DFR recording mode) | Substation | Medium
continuous fault recorder | DFR_DDR_001 |  | IDM+ continuous fault recording function | Substation | Medium
DFR | DFR_DDR_001 | MET_SAMPLING_RATE | Digital Fault Recorder | Substation / feeder | High
digital fault recorder | DFR_DDR_001 |  | Digital fault recording device | Substation | High
DFR panel | DFR_DDR_001; FMS_001 |  | Fault recording panel housing IDM+ and accessories | Substation panel | High
FRS panel | DFR_DDR_001; FMS_001 |  | Fault Recording System panel | Substation | High
FRS | DFR_DDR_001 |  | Fault Recording System (generic term for DFR system) | Substation | High
fault recording system | DFR_DDR_001 |  | Generic: fault recording system installed at substation | Substation | High
fault disturbance recorder | DFR_DDR_001 |  | Combined fault and disturbance recorder | Substation | High
disturbance monitor | DFR_DDR_001 |  | Power system disturbance monitoring | Substation / grid | Medium
IDM+ 9 | DFR_DDR_001 | MET_ANALOG_CHANNELS | IDM+ 9-channel variant (9A/32D, 3U) | Substation | High
IDM+ 18 | DFR_DDR_001 | MET_ANALOG_CHANNELS | IDM+ 18-channel variant (18A/64D, 6U) | Substation | High
IDM+ 36 | DFR_DDR_001 | MET_ANALOG_CHANNELS | IDM+ 36-channel variant (36A/128D, 6U) | Substation | High
IDM+ 9A | DFR_DDR_001 | MET_ANALOG_CHANNELS | IDM+ 9 analog channel configuration | Substation | High
IDM+ 18A | DFR_DDR_001 | MET_ANALOG_CHANNELS | IDM+ 18 analog channel configuration | Substation | High
IDM+ 36A | DFR_DDR_001 | MET_ANALOG_CHANNELS | IDM+ 36 analog channel configuration | Substation | High
SOE | DFR_DDR_001 |  | Sequence of Events recorder (function of IDM+) | Substation | Medium
sequence of events | DFR_DDR_001 |  | SOE recording of digital input state changes | Substation | Medium
waveform recorder | DFR_DDR_001 |  | Voltage/current waveform recording capability | Substation | Medium
WAMS | PMU_001; WAMS_001 | MET_REPORTING_RATE | Wide Area Monitoring System based on synchrophasors | Transmission grid | High
wide area monitoring | PMU_001; WAMS_001 |  | Wide-area phasor-based grid monitoring | Multi-site grid | High
wide area measurement | PMU_001; WAMS_001 |  | Wide Area Measurement System (IEEE C37.118) | Transmission grid | High
PDC | PMU_001; WAMS_001 |  | Phasor Data Concentrator (central collection point for PMU data) | Grid control center | High
phasor data concentrator | PMU_001; WAMS_001 |  | Central server for collecting and processing PMU data streams | Grid | High
IEEE C37.118 | PMU_001 | MET_REPORTING_RATE | IEEE standard for synchrophasor measurement | Grid / PMU | High
C37.118 | PMU_001 | MET_REPORTING_RATE | IEEE C37.118 PMU compliance standard | Grid / PMU | High
C37.118 2014 | PMU_001 |  | IEEE C37.118-2014 revised PMU standard | Grid / PMU | High
synchrophasor streaming | PMU_001 |  | Real-time phasor data streaming compliant with IEEE C37.118 | Grid | High
phasor measurement unit | PMU_001 | MET_REPORTING_RATE | Synchrophasor measurement device | Grid | High
PMU panel | PMU_001; FMS_001 |  | Panel housing PMU-enabled IDM+ devices | Substation | High
FMS | FMS_001; DFR_DDR_001 |  | Fault Monitoring System (iQ+ platform + DFR hardware at substation) | Multi-site grid | High
FL-8 | FAULT_LOC_001 | MET_LINE_COUNT | Qualitrol TWS FL-8 traveling wave fault locator (up to 8 lines) | Transmission line | High
FL-1 | FAULT_LOC_001 | MET_LINE_COUNT | Qualitrol TWS FL-1 single-line traveling wave fault locator | Transmission line | High
FL8 | FAULT_LOC_001 |  | TWS FL-8 fault locator abbreviation | Transmission line | High
FL1 | FAULT_LOC_001 |  | TWS FL-1 fault locator abbreviation | Transmission line | High
TWS FL-8 | FAULT_LOC_001 | MET_LINE_COUNT | Qualitrol TWS FL-8 product (modular, up to 8 lines) | Transmission line | High
TWS FL-1 | FAULT_LOC_001 |  | Qualitrol TWS FL-1 product (single-line, distributed substations) | Transmission line | High
linear coupler | FAULT_LOC_001 |  | CT secondary linear coupler for TWS traveling wave detection | Transmission line CT secondary | High
TWS card | FAULT_LOC_001 |  | TWS option card fitted in IDM+ for integrated fault location | Substation / IDM+ | High
FL2 | FAULT_LOC_001 | MET_LINE_COUNT | TWS FL-8 configured for 2-line monitoring (BOQ shorthand) | Transmission line | Medium
FL-2 | FAULT_LOC_001 | MET_LINE_COUNT | TWS FL-8 in 2-line configuration (site BOQ notation) | Transmission line | Medium
iQ+ | FMS_001; SUB_SOFT_001 |  | Qualitrol iQ+ Master Station software for DFR/TWS/PMU fleet management | Substation server | High
iQ plus | FMS_001; SUB_SOFT_001 |  | iQ+ Master Station (alternate spelling) | Substation server | High
master station | FMS_001; SUB_SOFT_001 |  | iQ+ centralized master station software | Substation server | High
iQ master station | FMS_001; SUB_SOFT_001 |  | Qualitrol iQ+ Master Station application | Substation server | High
CASHEL FMS | FMS_001 |  | CASHEL (Qualitrol brand name for FMS panels/server system) | Substation FMS | High
CASHEL server | FMS_001 |  | Rackmount server included in CASHEL FMS system | Substation server | High
FMS server | FMS_001 |  | Fault Management System server (iQ+ host) | Substation server | High
GridAssist | FMS_001; SUB_SOFT_001 |  | Qualitrol GridAssist substation monitoring platform | Substation / fleet | Medium
central server | FMS_001 |  | Central iQ+ server for multi-DFR data collection | Substation server | Medium
substation data server | FMS_001 |  | Server infrastructure for substation monitoring data management | Substation server | Medium
SmartSub | SUB_SOFT_001 |  | Qualitrol SmartSub substation asset performance management platform | Substation / fleet | High
PDMG-RH | GIS_PD_001 | MET_SENSOR_TYPE | Qualitrol PDMG-RH GIS PD monitoring system (Gen 3) | GIS | High
PDMG | GIS_PD_001 | MET_SENSOR_TYPE | PDMG series partial discharge monitor for GIS | GIS | High
GIS PDM | GIS_PD_001 |  | GIS Partial Discharge Monitor (generic abbreviation) | GIS | High
UHF coupler | GIS_PD_001 | MET_SENSOR_TYPE | UHF sensor/coupler installed on GIS for PD detection | GIS | High
OCU | GIS_PD_001 |  | Optical Converter Unit (signal conditioner in PDMG-RH system) | GIS PDM system | Medium
optical converter unit | GIS_PD_001 |  | OCU signal conditioning unit in PDMG-RH GIS PD system | GIS | Medium
arc detection | GIS_ARC_001; GIS_PD_001 |  | GIS arc flash/discharge detection capability (PDMG-RH Gen3 feature) | GIS | High
arc flash | GIS_ARC_001 |  | Arc flash event in GIS requiring detection and localization | GIS | High
flashover | GIS_ARC_001 |  | GIS internal flashover event (arc discharge) | GIS | High
GIS flashover | GIS_ARC_001 |  | Flashover in gas-insulated switchgear compartment | GIS | High
arc localization | GIS_ARC_001 |  | Pinpointing arc location in GIS compartment to enable fast bay re-energization | GIS | High
QBCM | BRK_HEALTH_001 |  | Qualitrol QBCM circuit breaker condition monitor | Circuit breaker | High
BCM | BRK_HEALTH_001 |  | Circuit breaker condition monitor (generic / Qualitrol product) | Circuit breaker | High
breaker condition monitor | BRK_HEALTH_001 |  | Online condition monitor for high-voltage circuit breakers | HV circuit breaker | High
CBT 200 | BRK_HEALTH_001 |  | Hathaway CBT 200 circuit breaker monitor | Circuit breaker | Medium
BCM 200 | BRK_HEALTH_001 |  | Hathaway BCM 200/200E circuit breaker monitor | Circuit breaker | Medium
INFORMA PMD-A | PQ_CLASSA_001 | MET_PQ_CLASS | Qualitrol INFORMA PMD-A Class A power quality monitor | PCC / bus / feeder | High
PMD-A | PQ_CLASSA_001 | MET_PQ_CLASS | INFORMA PMD-A power quality monitor (abbreviated) | PCC / feeder | High
INFORMA | PQ_CLASSA_001 |  | Qualitrol INFORMA series power quality monitors | PCC / bus | Medium
power system monitor | DFR_DDR_001; PQ_CLASSA_001 |  | Multifunction substation monitor (IDM+ / INFORMA PMD-A) | Substation | Medium
TM1 | TR_DGA_001 | MET_DGA_GAS_COUNT | Qualitrol Serveron TM1 single-gas DGA monitor | Transformer | High
TM3 | TR_DGA_001 | MET_DGA_GAS_COUNT | Qualitrol Serveron TM3 3-gas DGA monitor | Transformer | High
TM8 | TR_DGA_001 | MET_DGA_GAS_COUNT | Qualitrol Serveron TM8 8-gas DGA monitor | Transformer | High
Serveron | TR_DGA_001 |  | Qualitrol Serveron online DGA monitor series | Transformer | High
inter-area oscillation | WAMS_001; PMU_001 |  | Low-frequency power swing between grid areas (WAMS use case) | Transmission grid | High
power swing monitoring | WAMS_001; PMU_001 |  | Wide-area monitoring of power system oscillations | Transmission grid | High
frequency disturbance | WAMS_001; DFR_DDR_001 |  | System frequency deviation event (DFR or WAMS scope) | Grid | Medium

## 06_Product_Family_Master
Product Family Master - Product Families Before Actual Models
Use this as the first-level product candidate table. Actual product models should be added in the Product Master Template.
Product Family ID | Product Family | Applicable Scenario IDs | Primary Asset Type | Typical Capabilities | Default Quantity Rule ID | Dependencies / Required Inputs | Commercial / Engineering Notes
PF_DGA | Online DGA Monitor | TR_DGA_001 | Oil-filled transformer | Online dissolved gas monitoring; moisture; oil temperature; alarm outputs; SCADA integration | QR_TR_DGA_001 | Transformer count; oil type; gas count requirement; protocol; power supply | Actual product models and gas capabilities must be validated by product team.
PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Oil/winding temperature monitoring; fan/cooling control; alarm/trip contacts | QR_TR_TEMP_001 | Transformer count; temperature points; fan stages; alarm contacts | Differentiate oil-filled and dry-type transformer applications.
PF_BUSHING | Bushing Monitor | TR_BUSH_001 | Transformer bushing | Capacitance/tan delta/leakage current monitoring; phase comparison; alarms | QR_TR_BUSH_001 | Transformer count; bushing count; voltage level; phase configuration | Channel count must be confirmed.
PF_PD_TRANSFORMER | Transformer PD Monitor | TR_PD_001 | Power transformer | Partial discharge monitoring with selected sensor methods; alarm and trend monitoring | QR_TR_PD_001 | Transformer design; sensor type; monitoring zones; voltage level | Sensor placement requires engineering review.
PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Pressure relief; oil level; oil flow; Buchholz relay; contact outputs; environmental sensing | QR_TR_AUX_001 | Accessory list; mounting; contact type; alarm/trip logic | Often OEM or retrofit accessory scope.
PF_BREAKER | Circuit Breaker Monitor | BRK_HEALTH_001 | Circuit breaker | Trip/close timing; coil current; operation count; mechanism health; optional SF6 signals | QR_BRK_001 | Breaker count; breaker type; coil voltage; auxiliary contacts; SF6 requirement | One monitor per breaker is a default assumption only.
PF_GIS_PD | GIS PD Monitor | GIS_PD_001 | GIS bay | UHF partial discharge monitoring; bay/compartment monitoring; alarm/trend software | QR_GIS_PD_001 | GIS layout; bay count; compartments; voltage level; sensor placement | Do not finalize quantity without GIS layout.
PF_SWG_PD | MV Switchgear PD Monitor | SWG_PD_001 | MV switchgear | TEV/HFCT/UHF sensor options; feeder/panel PD monitoring; trend and alarms | QR_SWG_PD_001 | Panel count; feeder count; sensor type; voltage level | Scope may be panel-level or feeder-level.
PF_GEN_PD | Generator PD Monitor | GEN_PD_001 | Generator | Online/offline stator partial discharge monitoring; couplers/sensors; trends and alarms | QR_GEN_PD_001 | Generator count; voltage; rating; coupler count; online/offline mode | Iris Power-related product expertise required.
PF_GEN_EWV | Generator End-Winding Vibration Monitor | GEN_EWV_001 | Generator | End-winding vibration sensors; trend monitoring; alarms | QR_GEN_EWV_001 | Generator count; sensor locations; speed; vibration thresholds | Engineering review required.
PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Air gap monitoring; rotor flux; eccentricity; unit-level monitoring | QR_GEN_AIRGAP_001 | Hydro unit count; pole count; sensor layout; speed | Strongly drawing/design dependent.
PF_MOTOR | Motor Monitor | MTR_PD_001; MTR_TEMP_001 | Large motor | Motor PD; temperature; RTD/bearing temperature; condition monitoring | QR_MOTOR_001 | Motor list; voltage/rating; RTD count; criticality; sensor count | Prioritize critical large motors.
PF_PQ | Power Quality Recorder | PQ_CLASSA_001; RENEWABLE_PCC; DATA_CENTER_POWER | PCC / bus / feeder | Class A PQ; harmonics; flicker; sag/swell; transient event recording | QR_PQ_001 | PCC count; voltage/current channels; PQ class; standard; time sync | Class A requirement must be treated as must-have.
PF_DFR | Digital Fault / Disturbance Recorder | DFR_DDR_001; FAULT_LOC_001 | Substation / feeder / plant bus | Waveform/event recording; trigger logic; time synchronization; channel recording | QR_DFR_001 | Channel list; voltage/current inputs; sampling rate; trigger; time sync | Channel count drives configuration and quantity.
PF_PMU | Phasor Measurement Unit | PMU_001 | Grid measurement point | Synchrophasor measurement; reporting rate; time sync; grid monitoring | QR_PMU_001 | Measurement points; reporting rate; standard; time sync; channel count | May be standalone or integrated with recorder.
PF_SOFTWARE | Monitoring Software / Asset Platform | SUB_SOFT_001; COMM_SCADA_001 | Multi-asset / site / fleet | Dashboards; alarms; historian/SCADA integration; analytics; fleet view | QR_SOFT_001 | Site count; asset count; data points; protocol; license model | License model and commercial rules must be confirmed.
PF_GATEWAY | Communication Gateway / Integration Module | COMM_SCADA_001 | Monitoring system | Protocol conversion; SCADA interface; network connectivity; cybersecurity support | QR_GATEWAY_001 | Protocol; network topology; device count; cybersecurity constraints | May be accessory or stand-alone integration line.
PF_TWS | Traveling Wave Fault Locator | FAULT_LOC_001 | Transmission line / feeder | Traveling wave detection; single-end and double-end fault location; GPS/IEEE 1588 time sync; line protection relay integration; sub-cycle fault location accuracy | QR_FAULT_LOC_001 | Line count; line length (km); wave propagation velocity; GPS time-sync availability; CT/VT channel count; relay integration requirement | Qualitrol TWS FL-2 product confirmed in reference quotes. Confirm whether integrated with DFR or standalone. Verify channel count and line configuration.

## 07_Product_Master_Template
Product Master Template - Fill Actual Qualitrol Product Models
Actual product models, supported standards, protocols, and datasheet URLs are intentionally left blank where not available.
Product ID | Product Model | Product Family ID | Product Family | Applicable Scenario IDs | Primary Asset Type | Product Description | Supported Standards | Communication Protocols | Default Quantity Rule ID | Required Accessories | Optional Accessories | Datasheet URL | Source Owner | Status | Notes
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | Online DGA Monitor | TR_DGA_001 | Oil-filled transformer | Single-gas online DGA monitor that continuously monitors hydrogen PPM levels and can alarm based on PPM levels and/or Rate of Change (ROC) to warn operators of transformer faults. |  |  | QR_TR_DGA_001 |  |  | https://www.qualitrolcorp.com/products/TM1 |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | Online DGA Monitor | TR_DGA_001 | Oil-filled transformer | 3-gas online DGA monitor using gas chromatography to deliver lab-quality results and Duval triangle diagnostics. Measures the three Duval Triangle fault gases and can be used on conservator or nitrogen-blanketed transformers. |  |  | QR_TR_DGA_001 |  |  | https://www.qualitrolcorp.com/products/TM3 |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | Online DGA Monitor | TR_DGA_001 | Oil-filled transformer | Online gas chromatography DGA monitor measuring eight gases including hydrogen, carbon monoxide, methane, ethylene, ethane, and acetylene, with internal gas extraction system and helium carrier gas. |  |  | QR_TR_DGA_001 |  |  | https://offers.qualitrolcorp.com/hubfs/2017/Resource%20Library/810-1647-03_B%20Transformer%20Monitor%20-%20TM%20Series%20Site%20Prep%20Guide.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PD_TRANSFORMER_01 | QPDM | PF_PD_TRANSFORMER | Transformer PD Monitor | TR_PD_001 | Power transformer | Continuous online UHF Partial Discharge monitor for transformers with real-time PD amplitude and discharge rate monitoring, trending, and fault classification. IP66 rated enclosure with built-in LED indicators and remote client. | CIGRE life management guidelines |  | QR_TR_PD_001 |  |  | https://www.qualitrolcorp.com/products/QPDM |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PD_TRANSFORMER_02 | QPPDM | PF_PD_TRANSFORMER | Transformer PD Monitor | TR_PD_001 | Power transformer | Portable partial discharge monitor for transformers and GIS. |  |  | QR_TR_PD_001 |  |  | https://www.qualitrolcorp.com/products/QPPDM |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_BREAKER_01 | QBCM | PF_BREAKER | Circuit Breaker Monitor | BRK_HEALTH_001 | Circuit breaker | Advanced Circuit Breaker Monitoring System with intelligent analytics for monitoring breaker health including SF6 density trends, travel curves, coil current signatures, electrical wear calculations, and operating mechanism performance. | IEC 61850, COMTRADE | IEC 61850, COMTRADE | QR_BRK_001 |  |  | https://www.qualitrolcorp.com/products/QBCM |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_BREAKER_02 | QBCM Software | PF_BREAKER | Circuit Breaker Monitor | BRK_HEALTH_001 | Circuit breaker | Circuit Breaker Monitoring & Diagnostics Software for automated data processing, trend analysis, and predictive maintenance scheduling. | IEC 61850, COMTRADE | IEC 61850, COMTRADE | QR_BRK_001 |  |  | https://www.qualitrolcorp.com/products/QBCM-Software |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_BREAKER_03 | HATHAWAY CBT 200/400 | PF_BREAKER | Circuit Breaker Monitor | BRK_HEALTH_001 | Circuit breaker | Hathaway Breaker Condition Monitor listed in Qualitrol Product Overview Catalog under Breaker Condition Monitors. |  |  | QR_BRK_001 |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_BREAKER_04 | HATHAWAY BCM 200/200E | PF_BREAKER | Circuit Breaker Monitor | BRK_HEALTH_001 | Circuit breaker | Hathaway Breaker Condition Monitor listed in Qualitrol Product Overview Catalog under Breaker Condition Monitors. |  |  | QR_BRK_001 |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GIS_PD_01 | Gen 3 PDM | PF_GIS_PD | GIS PD Monitor | GIS_PD_001 | GIS bay | Online PD monitoring and Arc Monitor for GIS using UHF sensors with IEC 61850 support. | IEC 61850 | IEC 61850 | QR_GIS_PD_001 |  |  | https://www.qualitrolcorp.com/products/Gen3PDM |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GIS_PD_02 | PDMG-RH - Gen 3 | PF_GIS_PD | GIS PD Monitor | GIS_PD_001 | GIS bay | Qualitrol DMS PDMG-RH GIS Partial Discharge Monitor for UHF partial discharge monitoring of gas-insulated switchgear. |  |  | QR_GIS_PD_001 |  |  | https://www.qualitrolcorp.com/products/PDMG |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GIS_PD_03 | Portable PDM | PF_GIS_PD | GIS PD Monitor | GIS_PD_001 | GIS bay | Portable partial discharge monitor for transformers and GIS using UHF technology; hand-carry system with touch interface and intelligent data handling (SMARTSUB Software). |  | Ethernet (RJ45 10/100 Mbps), USB | QR_GIS_PD_001 |  |  | https://smsystems.co.in/qualitrol/pdf/PD-D27-10L-01E_Portable_PDM.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GIS_PD_04 | QPDM | PF_GIS_PD | GIS PD Monitor | GIS_PD_001 | GIS bay | Next generation UHF continuous online partial discharge monitor for transformers (related to GIS PD monitoring family); high dynamic range, real-time amplitude and discharge rate trending, IP66 enclosure. |  |  | QR_GIS_PD_001 |  |  | https://www.qualitrolcorp.com/products/QPDM |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MV Switchgear PD Monitor | SWG_PD_001 | MV switchgear | Continuous online UHF partial discharge monitor for transformers; real-time PD amplitude and discharge rate monitoring, trending and classification. | IEC 60270; CIGRE life management guidelines | Ethernet (RJ45/fiber); IEC 61850; Modbus | QR_SWG_PD_001 |  |  | https://www.qualitrolcorp.com/products/QPDM |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_SWG_PD_02 | QPPDM | PF_SWG_PD | MV Switchgear PD Monitor | SWG_PD_001 | MV switchgear | Qualitrol portable partial discharge monitor for transformer and GIS PD measurement. |  |  | QR_SWG_PD_001 |  |  | https://www.qualitrolcorp.com/products/QPPDM |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_SWG_PD_03 | PDMG-RH Gen 3 | PF_SWG_PD | MV Switchgear PD Monitor | SWG_PD_001 | MV switchgear | DMS PDMG-RH GIS partial discharge monitor (Generation 3) for gas insulated switchgear. |  |  | QR_SWG_PD_001 |  |  | https://www.qualitrolcorp.com/products/PDMG |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_SWG_PD_04 | IC44 | PF_SWG_PD | MV Switchgear PD Monitor | SWG_PD_001 | MV switchgear | Qualitrol IC44 UHF partial discharge coupler sensor for PD detection. |  |  | QR_SWG_PD_001 |  |  | https://www.qualitrolcorp.com/products/IC44 |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GEN_PD_01 | PDTracII 4208 | PF_GEN_PD | Generator PD Monitor | GEN_PD_001 | Generator | Continuous partial discharge measurement system for motors/generators using Iris Power Epoxy Mica Capacitor Couplers. |  |  | QR_GEN_PD_001 |  |  | https://www.qualitrolcorp.com/products/PDTracII |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GEN_PD_02 | TGA-S | PF_GEN_PD | Generator PD Monitor | GEN_PD_001 | Generator | Iris Power TGA-S turbo generator partial discharge analyzer/monitor for stator winding insulation condition assessment. |  |  | QR_GEN_PD_001 |  |  | https://www.qualitrolcorp.com/products/TGA-S |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GEN_EWV_01 | EVAII | PF_GEN_EWV | Generator End-Winding Vibration Monitor | GEN_EWV_001 | Generator | Iris Power EVAII fiber optic accelerometer vibration sensor kit for endwinding vibration monitoring on air-cooled machines. |  |  | QR_GEN_EWV_001 |  |  | https://www.qualitrolcorp.com/products/EVAII |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GEN_EWV_02 | GuardII+ | PF_GEN_EWV | Generator End-Winding Vibration Monitor | GEN_EWV_001 | Generator | Iris Power GuardII+ online instrument for continuous generator and motor condition based monitoring. |  |  | QR_GEN_EWV_001 |  |  | https://www.qualitrolcorp.com/products/GuardIIPlus |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GEN_EWV_03 | EVTracII | PF_GEN_EWV | Generator End-Winding Vibration Monitor | GEN_EWV_001 | Generator | Iris Power EVTracII online instrument for continuous end winding vibration monitoring. |  |  | QR_GEN_EWV_001 |  |  | https://offers.qualitrolcorp.com/direct-current |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GEN_AIRGAP_01 | Iris Power TFProbe | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Flexible sensor for rotor flux monitoring in motors and generators. | None | None | QR_GEN_AIRGAP_001 |  |  | https://www.qualitrolcorp.com/products/TFProbe |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GEN_AIRGAP_02 | Iris Power FFProbe | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Rotor flux sensor for synchronous machines used in rotor flux monitoring. | None | None | QR_GEN_AIRGAP_001 |  |  | https://www.qualitrolcorp.com/products/FFProbe |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GEN_AIRGAP_03 | Iris Power Capacitive Air Gap Sensor (CGS) | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Capacitive air gap sensor for continuous on-line air gap monitoring of hydro generators. Measures distance between rotor and stator; output directly proportional to air gap distance (pole profile). Kit includes probes, linearization modules, junction box and installation materials. | None | None | QR_GEN_AIRGAP_001 |  |  | https://irispower.com/wp-content/uploads/2016/11/Iris-Power-CGS-Brochure-Capacitive-Gap-Sensor-1.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GEN_AIRGAP_04 | Iris Power TGA-S | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Iris Power TGA monitor for generator stator winding partial discharge monitoring. | None | None | QR_GEN_AIRGAP_001 |  |  | https://www.qualitrolcorp.com/products/TGA-S |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GEN_AIRGAP_05 | Iris Power GuardII+ | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Iris Power GuardII+ continuous on-line partial discharge monitor for generators. | None | None | QR_GEN_AIRGAP_001 |  |  | https://www.qualitrolcorp.com/products/GuardIIPlus |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_MOTOR_01 | PDTracII 4208 | PF_MOTOR | Motor Monitor | MTR_PD_001; MTR_TEMP_001 | Large motor | System providing continuous partial discharge measurement in motors using Iris Power Epoxy Mica Capacitor Couplers | None | None | QR_MOTOR_001 |  |  | https://www.qualitrolcorp.com/products/PDTracII |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_MOTOR_02 | PPM-97 Corona Probe | PF_MOTOR | Motor Monitor | MTR_PD_001; MTR_TEMP_001 | Large motor | Offline partial discharge locator (corona probe) for motors and generators | None | None | QR_MOTOR_001 |  |  | https://www.qualitrolcorp.com/products/PPM-97 |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_MOTOR_03 | PPM-97 TGA-B | PF_MOTOR | Motor Monitor | MTR_PD_001; MTR_TEMP_001 | Large motor | Iris Power TGA monitor | None | None | QR_MOTOR_001 |  |  | https://www.qualitrolcorp.com/products/TGA-B |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PQ_01 | BEN 6000 | PF_PQ | Power Quality Recorder | PQ_CLASSA_001; RENEWABLE_PCC; DATA_CENTER_POWER | PCC / bus / feeder | Extreme digital fault recorder with optional Class A power quality monitoring; flexible upgradeable device usable as DFR, DSM, DDR, continuous recorder, Class A PQ meter, PMU, fault locator and SOE. Up to 192 analog channels and 384 digital channels in central or distributed architecture; up to 4 PQ cards in parallel. | IEC 61000-4-30 Class A; IEC 61000-3-6/7; IEC 61850; IEEE C37.111 COMTRADE; NERC compliant | IEC 61850 GOOSE | QR_PQ_001 |  |  | https://www.leane.it/sites/default/files/prodotti/BEN_6000.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PQ_02 | BEN 6000 PORTABLE | PF_PQ | Power Quality Recorder | PQ_CLASSA_001; RENEWABLE_PCC; DATA_CENTER_POWER | PCC / bus / feeder | Portable extreme digital fault recorder for temporary/quick disturbance system monitoring, power generation dynamic monitoring, fault recording, synchrophasor measurement, SOE and/or Class A power quality monitoring. 16 analog and 16 digital channels, expandable via remote acquisition units. | IEC 61000-4-30 Class A; IEC 61850 | IEC 61850 GOOSE | QR_PQ_001 |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PQ_03 | BEN 600 | PF_PQ | Power Quality Recorder | PQ_CLASSA_001; RENEWABLE_PCC; DATA_CENTER_POWER | PCC / bus / feeder | Extreme digital fault recorder for digital fault recording and power generation monitoring with multifunctional capabilities including disturbance system monitoring, synchrophasor measurement, SOE and/or Class A power quality monitoring. | IEC 61000-4-30 Class A; IEC 61850 | IEC 61850 GOOSE | QR_PQ_001 |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PQ_04 | IDM | PF_PQ | Power Quality Recorder | PQ_CLASSA_001; RENEWABLE_PCC; DATA_CENTER_POWER | PCC / bus / feeder | Hathaway IDM digital fault recorder for fault recording and dynamic monitoring; usable as DFR, disturbance system monitor, continuous fault recorder, synchrophasor measurement unit, impedance based fault locator and power quality monitoring. | Class A power quality (optional) | IEC 61850 GOOSE (optional) | QR_PQ_001 |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PQ_05 | IDM+ | PF_PQ | Power Quality Recorder | PQ_CLASSA_001; RENEWABLE_PCC; DATA_CENTER_POWER | PCC / bus / feeder | IDM+ multi-function power system monitor. |  |  | QR_PQ_001 |  |  | https://www.qualitrolcorp.com/products/IDMPlus |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PMU_01 | HATHAWAY IDM | PF_PMU | Phasor Measurement Unit | PMU_001 | Grid measurement point | Digital fault recorder with synchrophasor measurement unit capability, used as digital fault recorder, disturbance system monitor, continuous fault recorder, PMU, impedance based fault locator and power quality monitor. | IEEE C37.118; IEC 61850 | IEC 61850 Goose messaging | QR_PMU_001 |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PMU_02 | HATHAWAY IDM PORTABLE | PF_PMU | Phasor Measurement Unit | PMU_001 | Grid measurement point | Portable digital fault recorder for mobile digital fault recording and dynamic monitoring, supporting synchrophasor measurement, impedance based fault location and power quality monitoring. | IEEE C37.118; IEC 61850 | IEC 61850 Goose messaging | QR_PMU_001 |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PMU_03 | BEN 6000 PORTABLE | PF_PMU | Phasor Measurement Unit | PMU_001 | Grid measurement point | Portable extreme digital fault recorder for mobile fault recording and power generation monitoring, supporting synchrophasor measurement, sequence of events recording and Class A power quality monitoring. | IEEE C37.118; IEC 61850 | IEC 61850 Goose messaging | QR_PMU_001 |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_SOFTWARE_01 | ITM Remote | PF_SOFTWARE | Monitoring Software / Asset Platform | SUB_SOFT_001; COMM_SCADA_001 | Multi-asset / site / fleet | Advanced transformer life management software integrated with 509 ITM Intelligent Transformer Monitors, featuring proprietary TransLife technology for thermal modeling, life consumption analysis, and multi-winding monitoring. |  |  | QR_SOFT_001 |  |  | https://www.qualitrolcorp.com/knowledge-center/blogs/qualitrol-blog/asset-management-software |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_SOFTWARE_02 | SmartSub | PF_SOFTWARE | Monitoring Software / Asset Platform | SUB_SOFT_001; COMM_SCADA_001 | Multi-asset / site / fleet | Modular, scalable substation asset performance management platform integrating with existing infrastructure to provide comprehensive asset visibility through advanced sensor networks and intelligent analytics. |  |  | QR_SOFT_001 |  |  | https://www.qualitrolcorp.com/products/SmartSUB |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_SOFTWARE_03 | iQ+ Master Station | PF_SOFTWARE | Monitoring Software / Asset Platform | SUB_SOFT_001; COMM_SCADA_001 | Multi-asset / site / fleet | Unified data management platform providing centralized client-server management for Qualitrol's monitoring device portfolio including legacy and current equipment, with distributed communication managers and SCADA/enterprise integration. |  | SCADA industry-standard protocols | QR_SOFT_001 |  |  | https://www.qualitrolcorp.com/knowledge-center/blogs/qualitrol-blog/asset-management-software |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_SOFTWARE_04 | TMView | PF_SOFTWARE | Monitoring Software / Asset Platform | SUB_SOFT_001; COMM_SCADA_001 | Multi-asset / site / fleet | Qualitrol/Serveron transformer monitoring software dashboard. |  |  | QR_SOFT_001 |  |  | https://www.qualitrolcorp.com/products/TMView |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_SOFTWARE_05 | QTMS | PF_SOFTWARE | Monitoring Software / Asset Platform | SUB_SOFT_001; COMM_SCADA_001 | Multi-asset / site / fleet | Transformer Monitoring System with modular design and web-based software for condition based, continuous online monitoring of transformer health. Supports hot-swappable, field-upgradeable modules and interfaces with Qualitrol and third-party smart sensors. | IEC 61850; IEC 60870-104-5; DNP 3.0 (Level 3); Modbus | Serial: DNP 3.0 (Level3), Modbus, IEC 60870-104-5; Ethernet: IEC 61850, IEC 60870-104-5, DNP 3.0 (Level 3), Modbus | QR_SOFT_001 |  |  | https://vainstein-ingenieros.com/wp-content/uploads/2024/01/QTMS.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GATEWAY_01 | QGateway (GTW-SP-EP) | PF_GATEWAY | Communication Gateway / Integration Module | COMM_SCADA_001 | Monitoring system | Qualitrol compact and rugged IEC 61850 gateway providing direct serial link to IEC 61850 Smart Grid protocol; links up to two serial devices simultaneously and extends distance between control cabinets and control room using TCP/IP. Also supports Modbus, DNP 3.0 and IEC 60870-5-104. | IEC 61850; IEC 60870-5-104; IEC 61000-4-2/3/4/5/6/8; IEC 60255-5; IEEE C37.90; IEEE C37.90.1-2002; ISO 9001 | Modbus, DNP 3.0, IEC 61850, IEC 60870-5-104, HTTP (web server) | QR_GATEWAY_001 |  |  | http://www.neoptix.com/literature/ap-m09-21l-01a_qgateway_120509.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_DFR_01 | IDM+ | PF_DFR | Digital Fault / Disturbance Recorder | DFR_DDR_001; FAULT_LOC_001 | Substation / feeder / plant bus | Multifunctional Disturbance Fault Recorder integrating six recording functions: fast disturbance recording, slow disturbance recording, power quality monitoring, traveling wave fault location, sequence of event recording, and phasor measurement (PMU) streaming. | None | None | QR_DFR_001 |  |  | https://www.qualitrolcorp.com/knowledge-center/blogs/qualitrol-blog/multifunctional-fault-recorder | Tavily research (pending review) | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_DFR_02 | iQ+ | PF_DFR | Digital Fault / Disturbance Recorder | DFR_DDR_001; FAULT_LOC_001 | Substation / feeder / plant bus | iQ+ Master Station Software for managing fault/disturbance recording data across the power grid. | None | None | QR_DFR_001 |  |  | https://www.qualitrolcorp.com/products/IQPlus | Tavily research (pending review) | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_TWS_01 | HATHAWAY MARK VI | PF_TWS | Traveling Wave Fault Locator | FAULT_LOC_001 | High voltage transmission line | Traveling wave fault locator for single-end or double-end fault location on high-voltage transmission lines. Supports up to 8 monitored lines per device with DNP 3.0 SCADA interface. |  | DNP 3.0 |  |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf | Tavily research (pending review) | Verified | Sourced via Tavily; verify model name and availability.
PROD_PF_TWS_02 | HATHAWAY DSFL | PF_TWS | Traveling Wave Fault Locator | FAULT_LOC_001 | High voltage transmission line | Digital Single-ended Fault Locator; traveling wave based; suitable for single-end fault location without GPS synchronization requirement at remote end. | [5 empty] | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf | Tavily research (pending review) | Verified | Sourced via Tavily; verify model name and availability.
PROD_PF_TWS_03 | IDM+ (TWS function) | PF_TWS | Traveling Wave Fault Locator | FAULT_LOC_001; DFR_DDR_001; PMU_001 | Transmission line | IDM+ multi-function recorder with integrated traveling wave fault location capability, GPS time reference with 100 ns precision time tagging. | [5 empty] | https://www.qualitrolcorp.com/knowledge-center/blogs/qualitrol-blog/traveling-wave-fault-location | Tavily research (pending review) | Verified | Sourced via Tavily; IDM+ covers DFR+PMU+TWS in one device. Verify licensing.
PROD_PF_DFR_03 | IDM+ 9 | PF_DFR | Digital Fault / Disturbance Recorder | DFR_DDR_001; PMU_001; FAULT_LOC_001; PQ_CLASSA_001 | Substation / feeder / plant bus | IDM+ 9: 9 analog and 32 digital channels (3U, 19-inch rack). Smallest IDM+ variant. Functions: DFR (512 samples/cycle), DDR, optional PMU (IEEE C37.118 2014), optional TWS card (±60m FL), optional Class A PQ (IEC 61000-4-30 Class A Ed.2). | IEEE C37.118-2014; IEC 61000-4-30 Class A; IEC 61850 | IEC 61850; IEC 60870-5-104; DNP 3.0; Modbus | QR_DFR_001 |  | GPS antenna; IRIG-B module; GPS splitter | https://www.qualitrolcorp.com/products/IDMPlus | Verified via Tavily web research + Gemba Samples BOQ/product manuals. | Verified | BOQ shorthand: IDM+ 9A/32D. 3U rackmount. Weight 15 kg. Sampling: 30.7 kHz@60Hz / 25.6 kHz@50Hz. Storage: 4 GB (opt. 16 GB). GPS time tagging: 100 ns.
PROD_PF_DFR_04 | IDM+ 18 | PF_DFR | Digital Fault / Disturbance Recorder | DFR_DDR_001; PMU_001; FAULT_LOC_001; PQ_CLASSA_001 | Substation / feeder / plant bus | IDM+ 18: 18 analog and 64 digital channels (6U, 19-inch rack). Mid-range IDM+ variant for substations with more feeders. Same optional functions as IDM+ 9 (PMU, TWS, Class A PQ). | IEEE C37.118-2014; IEC 61000-4-30 Class A; IEC 61850 | IEC 61850; IEC 60870-5-104; DNP 3.0; Modbus | QR_DFR_001 |  | GPS antenna; IRIG-B; TWS card (optional) | https://www.qualitrolcorp.com/products/IDMPlus | Verified via Tavily web research + Gemba Samples BOQ/product manuals. | Verified | BOQ shorthand: IDM+ 18A/64D. 6U rackmount. Weight 23 kg. Two 9-channel analog blocks. Suitable for 5–8 feeder substations.
PROD_PF_DFR_05 | IDM+ 36 | PF_DFR | Digital Fault / Disturbance Recorder | DFR_DDR_001; PMU_001; FAULT_LOC_001; PQ_CLASSA_001 | Substation / feeder / plant bus | IDM+ 36: 36 analog and 128 digital channels (6U, 19-inch rack). Largest standard IDM+ variant for substations with many feeders. Same optional functions (PMU, TWS, Class A PQ). | IEEE C37.118-2014; IEC 61000-4-30 Class A; IEC 61850 | IEC 61850; IEC 60870-5-104; DNP 3.0; Modbus | QR_DFR_001 |  | GPS antenna; IRIG-B; TWS card (optional) | https://www.qualitrolcorp.com/products/IDMPlus | Verified via Tavily web research + Gemba Samples BOQ/product manuals. | Verified | BOQ shorthand: IDM+ 36A/128D (or IDM+ 36A/64D for 64-DI variant). 6U rackmount. Four 9-channel analog blocks. Suitable for 10–12 feeder substations.
PROD_PF_TWS_04 | TWS FL-8 | PF_TWS | Traveling Wave Fault Locator | FAULT_LOC_001 | High-voltage transmission line / centralized relay room | TWS FL-8: modular traveling wave fault locator for centralized relay rooms. Monitors 2, 4, 6, or 8 transmission line ends (expandable in steps of 2). Uses linear coupler transducers on CT secondary wiring. GPS time tagging for double-ended fault location. Best accuracy ±60 m (±195 ft) independent of line length and impedance. | IEC 61850; GPS IEEE 1588 (optional) | DNP 3.0; iQ+ Master Station; serial; TCP/IP | QR_TWS_001 | Linear couplers (LC); GPS antenna and cable | iQ+ software | http://hvtest.co.za/Company/PDF/Qualitrol/TWS_FL8_FL1.pdf | Verified via Tavily web research + Gemba Samples BOQ/product manuals. | Verified | 3U, 19-inch rack. 132.5 mm H × 487 mm W × 362.2 mm D. 11 kg. Sample rate: 20 MHz. Channels: 3 per line (one per phase), 12-bit ADC. BOQ note: 'TWS FL-2' = FL-8 unit configured for 2 lines (not a separate model).
PROD_PF_TWS_05 | TWS FL-1 | PF_TWS | Traveling Wave Fault Locator | FAULT_LOC_001 | High-voltage transmission line / distributed substation | TWS FL-1: fixed-format single-line traveling wave fault locator. Designed for distributed substations monitoring one line end. Same technology as FL-8; fixed 1-line capacity. Accuracy ±60 m (±195 ft). |  | DNP 3.0; iQ+ Master Station | QR_TWS_001 | Linear couplers (1 set); GPS antenna |  | http://hvtest.co.za/Company/PDF/Qualitrol/TWS_FL8_FL1.pdf | Verified via Tavily web research + Gemba Samples BOQ/product manuals. | Verified | Fixed format (not modular). One line module only. Used when each substation monitors only one transmission line end. FL-8 is preferred for substations with multiple line ends.
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | Power Quality Recorder | PQ_CLASSA_001 | PCC / bus / feeder / distribution substation | Qualitrol INFORMA PMD-A: Class A power quality and fault recording device. Single device eliminates 90% of analytical time. 9 configurable analog channels (3U) or 9/18/27/36 channels (6U). Compliant with IEC 61000-4-30 Class A Ed.2 and IEC 61000-3-6/7 (EN 50160). | IEC 61000-4-30 Class A Ed.2; IEC 61000-3-6; IEC 61000-3-7; EN 50160 | Serial; Ethernet; Modbus; IEC 61850 (optional) | QR_PQ_001 |  | GPS time sync module | http://www.hvtest.co.za/Company/PDF/Qualitrol/PMD_A.pdf | Verified via Tavily web research + Gemba Samples BOQ/product manuals. | Verified | 3U (9ch) or 6U (9-36ch). Sampling: 25.6 kHz@50Hz, 30.72 kHz@60Hz. Storage: 4 GB CF (opt. 16 GB). Calibration: once every 5 years. Primary PQ-focused product (vs IDM+ which is DFR-focused).
PROD_PF_PMU_04 | IDM+ (PMU option) | PF_PMU | Phasor Measurement Unit | PMU_001; DFR_DDR_001; WAMS_001 | Transmission grid measurement point / substation bus / feeder | IDM+ with PMU option enabled: provides synchrophasor streaming per IEEE C37.118-2014 alongside full DFR/DDR functions. Available in 9, 18, or 36 analog channel variants. Used in FMS+WAMS deployments across GCC and international utilities. | IEEE C37.118-2014; IEC 61850; IEC 61000-4-30 Class A | IEC 61850 GOOSE; DNP 3.0; Modbus TCP; C37.118 streaming | QR_PMU_001 | GPS antenna; iQ+ Master Station software |  | https://www.qualitrolcorp.com/products/IDMPlus | Verified via Tavily web research + Gemba Samples BOQ/product manuals. | Verified | PMU is an optional add-on license/card for IDM+ 9/18/36. Reporting rates: 25 or 50 fps at 50 Hz; 30 or 60 fps at 60 Hz (typical). Used by GCCIA, OETC, Scottish Power, Statnett, EGAT, etc.

## 08_Product_Parameter_Template
Product Parameter Template - One Row Per Product Parameter
Avoid wide columns such as Parameter 1/2/3. Use this normalized table for matching.
Product ID | Product Model | Product Family ID | Parameter ID | Parameter Name | Min Value | Max Value | Supported Value / Text | Unit | Match Type | Match Priority | Evidence Source / Datasheet URL | Notes
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | MET_DGA_GAS_COUNT | DGA Gas Count | 1 | 1 | 1 | count |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | MET_DGA_GAS_SPECIES | DGA Gas Species |  |  | Hydrogen (H2) | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | MET_ALARM_THRESHOLD | Alarm Threshold |  |  | PPM level and/or Rate of Change (ROC) | varies |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | MET_ASSET_TYPE | Asset Type |  |  | Oil-filled transformer | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_DGA_GAS_COUNT | DGA Gas Count | 3 | 3 | 3 | count |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_DGA_GAS_SPECIES | DGA Gas Species |  |  | Methane (CH4), Ethylene (C2H4), Acetylene (C2H2) | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_SENSOR_TYPE | Sensor Type |  |  | Gas chromatography | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_ASSET_TYPE | Asset Type |  |  | Conservator or nitrogen-blanketed oil-filled transformer | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_DGA_GAS_COUNT | DGA Gas Count | 8 | 8 | 8 | count |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_DGA_GAS_SPECIES | DGA Gas Species |  |  | CO, CH4, C2H4, C2H6, C2H2 (and additional gases) | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_SENSOR_TYPE | Sensor Type |  |  | Gas chromatography | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_ASSET_TYPE | Asset Type |  |  | Conservator or nitrogen-blanketed oil-filled transformer | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PD_TRANSFORMER_01 | QPDM | PF_PD_TRANSFORMER | MET_ASSET_TYPE | Asset Type |  |  | Power transformer | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PD_TRANSFORMER_01 | QPDM | PF_PD_TRANSFORMER | MET_SENSOR_TYPE | Sensor Type |  |  | UHF | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PD_TRANSFORMER_01 | QPDM | PF_PD_TRANSFORMER | MET_PD_LEVEL | Built-in Sensitivity |  | -80 | -80 dBm sensitivity, 70 dB dynamic range, 300-2100 MHz band | dBm |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PD_TRANSFORMER_01 | QPDM | PF_PD_TRANSFORMER | MET_ENCLOSURE_RATING | Enclosure Rating |  |  | IP66 | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PD_TRANSFORMER_02 | QPPDM | PF_PD_TRANSFORMER | MET_ASSET_TYPE | Asset Type |  |  | Power transformer / GIS | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PD_TRANSFORMER_02 | QPPDM | PF_PD_TRANSFORMER | MET_SENSOR_TYPE | Sensor Type |  |  | UHF PD | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_01 | QBCM | PF_BREAKER | MET_ASSET_TYPE | Asset Type |  |  | Circuit breaker | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_01 | QBCM | PF_BREAKER | MET_COIL_CURRENT | Coil Current Signature |  |  | Coil current signature monitoring | A |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_01 | QBCM | PF_BREAKER | MET_TRIP_CLOSE_TIME | Travel Curve / Operating Time |  |  | Travel curves and operating mechanism timing | ms |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_01 | QBCM | PF_BREAKER | MET_SF6_PRESSURE | SF6 Density Trend |  |  | SF6 density trend monitoring | density |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_01 | QBCM | PF_BREAKER | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850, COMTRADE | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_02 | QBCM Software | PF_BREAKER | MET_ASSET_TYPE | Asset Type |  |  | Circuit breaker | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_02 | QBCM Software | PF_BREAKER | MET_LICENSE_SCOPE | Software License Scope |  |  | Diagnostics and analytics software for breaker fleet | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_03 | HATHAWAY CBT 200/400 | PF_BREAKER | MET_ASSET_TYPE | Asset Type |  |  | Circuit breaker | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_04 | HATHAWAY BCM 200/200E | PF_BREAKER | MET_ASSET_TYPE | Asset Type |  |  | Circuit breaker | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_01 | Gen 3 PDM | PF_GIS_PD | MET_SENSOR_TYPE | Sensor Type |  |  | UHF sensors | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_01 | Gen 3 PDM | PF_GIS_PD | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850 | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_01 | Gen 3 PDM | PF_GIS_PD | MET_ASSET_TYPE | Asset Type |  |  | GIS | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_02 | PDMG-RH - Gen 3 | PF_GIS_PD | MET_SENSOR_TYPE | Sensor Type |  |  | UHF | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_02 | PDMG-RH - Gen 3 | PF_GIS_PD | MET_ASSET_TYPE | Asset Type |  |  | GIS | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_03 | Portable PDM | PF_GIS_PD | MET_SENSOR_TYPE | Sensor Type |  |  | UHF, Wideband 300-1500 MHz | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_03 | Portable PDM | PF_GIS_PD | MET_SENSOR_COUNT | UHF Channels |  |  | 6 UHF channels + 1 noise antenna channel | count |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_03 | Portable PDM | PF_GIS_PD | MET_PD_LEVEL | PD Sensitivity |  |  | < 5 pC | pC |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_03 | Portable PDM | PF_GIS_PD | MET_SAMPLING_RATE | Sampling Rate |  |  | 15.4 KS/s per channel; total 107.5 KS/s for 7 channels (also 51000 samples per second cited) | samples/s |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_03 | Portable PDM | PF_GIS_PD | MET_POWER_SUPPLY | Power Supply |  |  | 90 to 264 VAC, 47-63 Hz; 40 to 290 VDC universal supply | V AC/DC |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_03 | Portable PDM | PF_GIS_PD | MET_NETWORK | Network Interface |  |  | RJ45 (10/100 Mbps), USB | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_03 | Portable PDM | PF_GIS_PD | MET_ALARM_THRESHOLD | Alarm Indications |  |  | PD fault alarm, PD alarm, PD warning alarm, system status | varies |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_04 | QPDM | PF_GIS_PD | MET_SENSOR_TYPE | Sensor Type |  |  | UHF | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_04 | QPDM | PF_GIS_PD | MET_PD_LEVEL | Dynamic Range |  |  | 70 dB | dB |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_04 | QPDM | PF_GIS_PD | MET_ENCLOSURE_RATING | Enclosure Rating |  |  | IP66 | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_SENSOR_TYPE | Sensor Type |  |  | UHF | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_SENSOR_COUNT | UHF Sensor Inputs | 1 | 24 | 1–6 channels, expandable to 24 | count |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_PD_LEVEL | Dynamic Range / Sensitivity |  |  | 70 dB dynamic range; sensitivity -75 to -80 dBm | dB |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_SAMPLING_RATE | Sampling Rate |  |  | 15,360 samples/s @ 60 Hz | samples/s |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_ENCLOSURE_RATING | Environmental Rating |  |  | IP66 | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_AMBIENT_TEMP | Operating Temperature Range | -25 | 55 | -25°C to +55°C | °C |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_HUMIDITY | Humidity | 5 | 95 | 5–95% | %RH |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850, Modbus | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_NETWORK | Network Interface |  |  | Ethernet (RJ45/fiber) | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_02 | QPPDM | PF_SWG_PD | MET_SENSOR_TYPE | Sensor Type |  |  | UHF | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_03 | PDMG-RH Gen 3 | PF_SWG_PD | MET_SENSOR_TYPE | Sensor Type |  |  | UHF | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_04 | IC44 | PF_SWG_PD | MET_SENSOR_TYPE | Sensor Type |  |  | UHF coupler | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_PD_01 | PDTracII 4208 | PF_GEN_PD | MET_SENSOR_TYPE | Sensor Type |  |  | Iris Power Epoxy Mica Capacitor Couplers | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_PD_01 | PDTracII 4208 | PF_GEN_PD | MET_PD_LEVEL | Partial Discharge Monitoring |  |  | Continuous online PD measurement | pC / mV / dB |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_PD_01 | PDTracII 4208 | PF_GEN_PD | MET_ASSET_TYPE | Asset Type |  |  | Generator/Motor | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_PD_02 | TGA-S | PF_GEN_PD | MET_ASSET_TYPE | Asset Type |  |  | Generator (turbo) | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_PD_02 | TGA-S | PF_GEN_PD | MET_PD_LEVEL | Partial Discharge Monitoring |  |  | Stator winding PD analysis | pC / mV / dB |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_EWV_01 | EVAII | PF_GEN_EWV | MET_SENSOR_TYPE | Sensor Type |  |  | Fiber optic accelerometer (all dielectric, no metallic parts) | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_EWV_01 | EVAII | PF_GEN_EWV | MET_VIBRATION | Vibration Dynamic Range | 0 | 50 | 0-50 g, resolution <0.007 g | g |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_EWV_01 | EVAII | PF_GEN_EWV | MET_AMBIENT_TEMP | Operating Temperature Range | -50 | 200 | -50°C to +200°C | °C |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_EWV_02 | GuardII+ | PF_GEN_EWV | MET_ASSET_TYPE | Asset Type |  |  | Generator and Motor | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_EWV_03 | EVTracII | PF_GEN_EWV | MET_ASSET_TYPE | Asset Type |  |  | Generator | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_01 | Iris Power TFProbe | PF_GEN_AIRGAP | MET_SENSOR_TYPE | Sensor Type |  |  | Rotor flux probe | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_01 | Iris Power TFProbe | PF_GEN_AIRGAP | MET_ROTOR_FLUX | Rotor Flux |  |  | Rotor flux monitoring | text/relative |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_01 | Iris Power TFProbe | PF_GEN_AIRGAP | MET_ASSET_TYPE | Asset Type |  |  | Motors and generators | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_02 | Iris Power FFProbe | PF_GEN_AIRGAP | MET_SENSOR_TYPE | Sensor Type |  |  | Rotor flux sensor | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_02 | Iris Power FFProbe | PF_GEN_AIRGAP | MET_ROTOR_FLUX | Rotor Flux |  |  | Rotor flux monitoring | text/relative |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_02 | Iris Power FFProbe | PF_GEN_AIRGAP | MET_ASSET_TYPE | Asset Type |  |  | Synchronous machines | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_03 | Iris Power Capacitive Air Gap Sensor (CGS) | PF_GEN_AIRGAP | MET_SENSOR_TYPE | Sensor Type |  |  | Capacitive gap probe with linearization module | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_03 | Iris Power Capacitive Air Gap Sensor (CGS) | PF_GEN_AIRGAP | MET_AIR_GAP | Air Gap |  |  | Output directly proportional to air gap distance (pole profile) | mm / % |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_03 | Iris Power Capacitive Air Gap Sensor (CGS) | PF_GEN_AIRGAP | MET_ENCLOSURE_RATING | Case Protection Class |  |  | IP66 | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_03 | Iris Power Capacitive Air Gap Sensor (CGS) | PF_GEN_AIRGAP | MET_ASSET_TYPE | Asset Type |  |  | Hydro generator | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_04 | Iris Power TGA-S | PF_GEN_AIRGAP | MET_PD_LEVEL | Partial Discharge Level |  |  | Stator winding partial discharge monitoring | pC / mV / dB |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_04 | Iris Power TGA-S | PF_GEN_AIRGAP | MET_ASSET_TYPE | Asset Type |  |  | Generator | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_05 | Iris Power GuardII+ | PF_GEN_AIRGAP | MET_PD_LEVEL | Partial Discharge Level |  |  | Online partial discharge monitoring | pC / mV / dB |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_05 | Iris Power GuardII+ | PF_GEN_AIRGAP | MET_ASSET_TYPE | Asset Type |  |  | Generator | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_MOTOR_01 | PDTracII 4208 | PF_MOTOR | MET_ASSET_TYPE | Asset Type |  |  | Large motor | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_MOTOR_01 | PDTracII 4208 | PF_MOTOR | MET_SENSOR_TYPE | PD Coupler Type |  |  | Iris Power Epoxy Mica Capacitor Couplers | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_MOTOR_01 | PDTracII 4208 | PF_MOTOR | MET_PD_LEVEL | Partial Discharge Measurement |  |  | Continuous PD measurement | pC / mV / dB |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_MOTOR_02 | PPM-97 Corona Probe | PF_MOTOR | MET_ASSET_TYPE | Asset Type |  |  | Motors & Generators | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_MOTOR_02 | PPM-97 Corona Probe | PF_MOTOR | MET_PD_LEVEL | Partial Discharge Detection |  |  | Offline PD location | pC / mV / dB |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_01 | BEN 6000 | PF_PQ | MET_PQ_CLASS | Power Quality Class |  |  | Class A (IEC 61000-4-30) | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_01 | BEN 6000 | PF_PQ | MET_SAG_SWELL | Sag / Swell Recording |  |  | PQ event detection, capture and trends | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_01 | BEN 6000 | PF_PQ | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850 GOOSE | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_01 | BEN 6000 | PF_PQ | MET_NETWORK | Network Interface |  |  | Ethernet/LAN | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_02 | BEN 6000 PORTABLE | PF_PQ | MET_PQ_CLASS | Power Quality Class |  |  | Class A | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_02 | BEN 6000 PORTABLE | PF_PQ | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850 GOOSE | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_03 | BEN 600 | PF_PQ | MET_PQ_CLASS | Power Quality Class |  |  | Class A | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_03 | BEN 600 | PF_PQ | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850 GOOSE | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_04 | IDM | PF_PQ | MET_PQ_CLASS | Power Quality Class |  |  | Class A (optional) | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_01 | HATHAWAY IDM | PF_PMU | MET_CURRENT_CHANNELS | Analog channels (max) |  | 192 | Up to 192 analog channels | count |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_01 | HATHAWAY IDM | PF_PMU | MET_PQ_CLASS | Power Quality Class |  |  | Class A | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_01 | HATHAWAY IDM | PF_PMU | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850 Goose messaging | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_02 | HATHAWAY IDM PORTABLE | PF_PMU | MET_CURRENT_CHANNELS | Analog channels (max) |  | 192 | Up to 192 analog channels | count |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_02 | HATHAWAY IDM PORTABLE | PF_PMU | MET_PQ_CLASS | Power Quality Class |  |  | Class A | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_02 | HATHAWAY IDM PORTABLE | PF_PMU | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850 Goose messaging | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_03 | BEN 6000 PORTABLE | PF_PMU | MET_CURRENT_CHANNELS | Analog channels |  | 16 | 16 analog channels, expandable via remote acquisition units | count |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_03 | BEN 6000 PORTABLE | PF_PMU | MET_PQ_CLASS | Power Quality Class |  |  | Class A | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_03 | BEN 6000 PORTABLE | PF_PMU | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850 Goose messaging | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_01 | ITM Remote | PF_SOFTWARE | MET_ASSET_TYPE | Asset Type |  |  | Transformer | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_01 | ITM Remote | PF_SOFTWARE | MET_LICENSE_SCOPE | Software License Scope |  |  | Transformer fleet life management software | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_02 | SmartSub | PF_SOFTWARE | MET_ASSET_TYPE | Asset Type |  |  | Substation / multi-asset | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_02 | SmartSub | PF_SOFTWARE | MET_LICENSE_SCOPE | Software License Scope |  |  | Substation asset performance management | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_03 | iQ+ Master Station | PF_SOFTWARE | MET_ASSET_TYPE | Asset Type |  |  | Multi-asset / fleet | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_03 | iQ+ Master Station | PF_SOFTWARE | MET_PROTOCOL | Communication Protocol |  |  | SCADA and enterprise asset management integration via industry-standard protocols | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_03 | iQ+ Master Station | PF_SOFTWARE | MET_LICENSE_SCOPE | Software License Scope |  |  | Enterprise / large installations | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_04 | TMView | PF_SOFTWARE | MET_ASSET_TYPE | Asset Type |  |  | Transformer | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_05 | QTMS | PF_SOFTWARE | MET_ASSET_TYPE | Asset Type |  |  | Transformer | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_05 | QTMS | PF_SOFTWARE | MET_PROTOCOL | Communication Protocol |  |  | DNP 3.0 (Level3), Modbus, IEC 60870-104-5, IEC 61850 | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_05 | QTMS | PF_SOFTWARE | MET_NETWORK | Network Interface |  |  | Serial; Ethernet | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_05 | QTMS | PF_SOFTWARE | MET_REPORTING_RATE | Data Logging / Store Rate |  |  | 100 variables; store rates 1 minute to 24 hours; 32 parameters at 15 second capture rate for 90 days (4 GB memory) | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GATEWAY_01 | QGateway (GTW-SP-EP) | PF_GATEWAY | MET_ASSET_TYPE | Asset Type |  |  | Monitoring system / protocol gateway | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GATEWAY_01 | QGateway (GTW-SP-EP) | PF_GATEWAY | MET_PROTOCOL | Communication Protocols |  |  | Modbus, DNP 3.0, IEC 61850, IEC 60870-5-104, HTTP | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GATEWAY_01 | QGateway (GTW-SP-EP) | PF_GATEWAY | MET_NETWORK | Network Interface |  |  | 2 x RS-485 Full-Duplex serial inputs; 1 x isolated RJ-45 Ethernet port | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GATEWAY_01 | QGateway (GTW-SP-EP) | PF_GATEWAY | MET_POWER_SUPPLY | Power Requirements |  |  | 24 VDC | V DC |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GATEWAY_01 | QGateway (GTW-SP-EP) | PF_GATEWAY | MET_AMBIENT_TEMP | Operating Temperature |  |  | Operating/storage temperature range (per datasheet) | °C |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_TIME_SYNC | Phasor Measurement Streaming |  |  | PMU phasor measurement streaming supported | text |  |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_DFR_02 | iQ+ | PF_DFR | MET_LICENSE_SCOPE | Master Station Software |  |  | Master station software scope | text |  |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_TWS_01 | HATHAWAY MARK VI | PF_TWS | MET_ASSET_COUNT | Lines Monitored per Device |  | 8 | Up to 8 lines | count |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf
PROD_PF_TWS_01 | HATHAWAY MARK VI | PF_TWS | MET_COMM_PROTOCOL | Communication Protocol |  |  | DNP 3.0; Modem; Ethernet
PROD_PF_TWS_03 | IDM+ (TWS function) | PF_TWS | MET_TIME_SYNC | Time Synchronization |  |  | GPS; 100 ns time tagging precision
PROD_PF_DFR_03 | Analog Channels | 9 | count | integer | 3U, single analog card block
PROD_PF_DFR_03 | Digital Channels | 32 | count | integer | 32 digital inputs standard
PROD_PF_DFR_03 | Form Factor | 3U (133 mm H × 483 mm W) | text | text | 19-inch rack mountable
PROD_PF_DFR_03 | DFR Sampling Rate | 512 samples/cycle (30.7 kHz@60Hz; 25.6 kHz@50Hz) | Hz | text | Selectable: 512/256/128/64/32 s/c
PROD_PF_DFR_03 | Analog Resolution | 20-bit current; 16-bit voltage/DC | bits | text
PROD_PF_DFR_03 | Accuracy | ±0.1% full scale | % | text
PROD_PF_DFR_03 | Data Storage | 4 GB CompactFlash standard; opt 8/16 GB | GB | text
PROD_PF_DFR_03 | Time Synchronization | GPS (100 ns); IRIG-B/J; 1 pps | ns | text
PROD_PF_DFR_03 | Operating Temperature | -5 to +50°C operating; -30 to +70°C storage | °C | text
PROD_PF_DFR_03 | Communication Protocol | IEC 61850; IEC 60870-5-104; DNP 3.0; Modbus | text | text
PROD_PF_DFR_03 | Optional Functions | PMU (IEEE C37.118-2014); TWS card (±60m FL); Class A PQ | text | text | Each option ordered separately
PROD_PF_DFR_03 | Asset Type | Substation bus / feeder / plant bus | text | text
PROD_PF_DFR_04 | Analog Channels | 18 | count | integer | 6U, two 9-channel analog blocks
PROD_PF_DFR_04 | Digital Channels | 64 | count | integer | 64 digital inputs standard
PROD_PF_DFR_04 | Form Factor | 6U (267 mm H × 483 mm W) | text | text | 19-inch rack mountable
PROD_PF_DFR_04 | DFR Sampling Rate | 512 samples/cycle (30.7 kHz@60Hz; 25.6 kHz@50Hz) | Hz | text
PROD_PF_DFR_04 | Data Storage | 4 GB CompactFlash standard; opt 8/16 GB | GB | text
PROD_PF_DFR_04 | Time Synchronization | GPS (100 ns); IRIG-B/J; 1 pps | ns | text
PROD_PF_DFR_04 | Communication Protocol | IEC 61850; IEC 60870-5-104; DNP 3.0; Modbus | text | text
PROD_PF_DFR_04 | Optional Functions | PMU (IEEE C37.118-2014); TWS card (±60m FL); Class A PQ | text | text
PROD_PF_DFR_04 | Operating Temperature | -5 to +50°C operating | °C | text
PROD_PF_DFR_04 | Asset Type | Substation bus / feeder / plant bus | text | text
PROD_PF_DFR_05 | Analog Channels | 36 | count | integer | 6U, four 9-channel analog blocks
PROD_PF_DFR_05 | Digital Channels | 128 | count | integer | 128 digital inputs standard
PROD_PF_DFR_05 | Form Factor | 6U (267 mm H × 483 mm W) | text | text | 19-inch rack mountable
PROD_PF_DFR_05 | DFR Sampling Rate | 512 samples/cycle (30.7 kHz@60Hz; 25.6 kHz@50Hz) | Hz | text
PROD_PF_DFR_05 | Data Storage | 4 GB standard; opt 8/16 GB | GB | text
PROD_PF_DFR_05 | Time Synchronization | GPS (100 ns); IRIG-B/J; 1 pps | ns | text
PROD_PF_DFR_05 | Communication Protocol | IEC 61850; IEC 60870-5-104; DNP 3.0; Modbus | text | text
PROD_PF_DFR_05 | Optional Functions | PMU (IEEE C37.118-2014); TWS card (±60m FL); Class A PQ | text | text
PROD_PF_DFR_05 | Operating Temperature | -5 to +50°C operating | °C | text
PROD_PF_DFR_05 | Asset Type | Substation bus / feeder / plant bus | text | text
PROD_PF_TWS_04 | Lines Monitored per Device | 2, 4, 6, or 8 (start 2, expand in steps of 2) | count | text | FL-8 starts with 2-line module
PROD_PF_TWS_04 | Fault Location Accuracy | ±60 m (±195 ft), independent of line length/impedance | m | text | Best accuracy up to 1000 km lines
PROD_PF_TWS_04 | Sample Rate | 20 MHz (also 10/5/2.5/1.25 MHz selectable) | MHz | text
PROD_PF_TWS_04 | Channels per Line | 3 (one per phase) from external linear coupler | count | integer | 12-bit ADC
PROD_PF_TWS_04 | Time Synchronization | GPS | text | text | Required for double-ended fault location
PROD_PF_TWS_04 | Communication Protocol | DNP 3.0; iQ+ Master Station; TCP/IP | text | text
PROD_PF_TWS_04 | Form Factor | 3U (132.5 mm H × 487 mm W × 362.2 mm D); 11 kg | text | text
PROD_PF_TWS_04 | Asset Type | HV transmission line (line end at substation) | text | text
PROD_PF_TWS_04 | Installation Method | Linear couplers on CT secondary; no line outage | text | text
PROD_PF_TWS_05 | Lines Monitored per Device | 1 | count | integer | Fixed format, single-line only
PROD_PF_TWS_05 | Fault Location Accuracy | ±60 m (±195 ft) | m | text
PROD_PF_TWS_05 | Time Synchronization | GPS | text | text
PROD_PF_TWS_05 | Communication Protocol | DNP 3.0; iQ+ Master Station | text | text
PROD_PF_TWS_05 | Application | Distributed substations monitoring one line end | text | text
PROD_PF_TWS_05 | Asset Type | HV transmission line (single end) | text | text
PROD_PF_PQ_06 | Power Quality Class | IEC 61000-4-30 Class A Edition 2.0 | text | text | Third-party certified
PROD_PF_PQ_06 | Analog Channels | 9 (3U) or 9/18/27/36 (6U, configurable) | count | text
PROD_PF_PQ_06 | Sampling Rate | 25.6 kHz@50Hz; 30.72 kHz@60Hz | Hz | text
PROD_PF_PQ_06 | Bandwidth | 25 to 4600 Hz ±0.5 dB | Hz | text
PROD_PF_PQ_06 | Standards | IEC 61000-4-30 Class A; IEC 61000-3-6/7; EN 50160 | text | text
PROD_PF_PQ_06 | Data Storage | 4 GB CF standard; opt 8/16 GB | GB | text
PROD_PF_PQ_06 | Communication Protocol | Serial; Ethernet; Modbus; IEC 61850 (opt.) | text | text
PROD_PF_PQ_06 | Asset Type | PCC / bus / feeder / distribution substation | text | text
PROD_PF_PMU_04 | Analog channels (max) | 9 / 18 / 36 (per IDM+ variant) | count | text
PROD_PF_PMU_04 | PMU Standard | IEEE C37.118-2014 | text | text
PROD_PF_PMU_04 | PMU Reporting Rate | 25 or 50 fps at 50 Hz; 30 or 60 fps at 60 Hz (typical) | fps | text
PROD_PF_PMU_04 | Time Synchronization | GPS (100 ns) | ns | text
PROD_PF_PMU_04 | Communication Protocol | IEEE C37.118 streaming; IEC 61850 GOOSE; DNP 3.0 | text | text
PROD_PF_PMU_04 | Optional Add-ons | TWS card (fault location); Class A PQ | text | text
PROD_PF_PMU_04 | Asset Type | Transmission grid measurement point / substation bus | text | text

## 09_Quantity_Rules
Quantity Rules - Explainable BOQ Quantity Logic
BOQ quantities should be derived from these rules plus the drawing/equipment-derived Asset List.
Quantity Rule ID | Scenario ID | Product Family ID | Product Family | Quantity Basis | Rule Description | Need Drawing | Need Asset List | Count Field | Example | Assumption / Risk
QR_TR_DGA_001 | TR_DGA_001 | PF_DGA | Online DGA Monitor | Transformer count | Default: 1 DGA monitor per monitored oil-filled transformer. | Recommended | Yes | transformer_count | Two oil-filled main transformers T1 and T2 => Qty 2 | Do not apply to dry-type transformers.
QR_TR_TEMP_001 | TR_TEMP_001; DRY_TR_TEMP_001 | PF_TR_TEMP | Transformer Temperature Monitor | Transformer count | Default: 1 temperature monitor per transformer or transformer control cabinet. | Optional | Yes | transformer_count | Three dry-type transformers => Qty 3 | Cooling stage/channel count may change configuration.
QR_TR_BUSH_001 | TR_BUSH_001 | PF_BUSHING | Bushing Monitor | Transformer count and bushing/channel count | Default: 1 system per transformer; channels depend on monitored bushing count. | Recommended | Yes | bushing_count | Two transformers with 6 bushings each => 2 systems / 12 channels | Needs bushing configuration.
QR_TR_PD_001 | TR_PD_001 | PF_PD_TRANSFORMER | Transformer PD Monitor | Monitoring zone / sensor count | Quantity depends on transformer design and selected PD sensor method. | Recommended | Yes | sensor_count | One transformer with 3 UHF sensors => Qty per engineering design | Requires product engineer review.
QR_TR_AUX_001 | TR_AUX_001 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | Accessory point count | Quantity equals required accessories or protection points per transformer. | Optional | Yes | accessory_count | One PRD + one oil level indicator per transformer | Accessory scope may be provided by OEM.
QR_BRK_001 | BRK_HEALTH_001 | PF_BREAKER | Circuit Breaker Monitor | Breaker count | Default: 1 breaker monitor per monitored circuit breaker. | Recommended | Yes | breaker_count | Six 220kV breakers => Qty 6 | Confirm whether one monitor can cover multiple mechanisms depending on product architecture.
QR_GIS_PD_001 | GIS_PD_001 | PF_GIS_PD | GIS PD Monitor | GIS bay / compartment / monitoring zone count | Quantity based on GIS layout, bays, compartments, and sensor placement. | Strongly Required | Yes | gis_bay_count | Eight GIS bays with defined UHF sensor locations => engineering-derived Qty | Do not estimate without GIS layout.
QR_SWG_PD_001 | SWG_PD_001 | PF_SWG_PD | MV Switchgear PD Monitor | Panel / feeder / sensor count | Quantity depends on switchgear lineup and panel/feeder coverage. | Required | Yes | panel_count | Twelve MV panels => Qty depends on panel-level or group-level design | Scope must define feeder vs lineup coverage.
QR_GEN_PD_001 | GEN_PD_001 | PF_GEN_PD | Generator PD Monitor | Generator unit count | Default: 1 monitoring system per generator; sensor/coupler count per design. | Recommended | Yes | generator_count | Four generator units => Qty 4 systems plus couplers | Coupler count requires generator design review.
QR_GEN_EWV_001 | GEN_EWV_001 | PF_GEN_EWV | Generator End-Winding Vibration Monitor | Generator unit and sensor location count | Quantity based on generator units and end-winding sensor locations. | Required | Yes | sensor_count | One generator with 12 vibration sensors => Qty per system/channel capacity | Engineering review required.
QR_GEN_AIRGAP_001 | GEN_AIRGAP_001 | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | Hydro unit count and sensor layout | Quantity based on each hydro unit and air gap/flux sensor layout. | Required | Yes | generator_count | Two hydro units => two systems plus sensor sets | Design-specific.
QR_MOTOR_001 | MTR_PD_001; MTR_TEMP_001 | PF_MOTOR | Motor Monitor | Critical motor count and channel count | Default: 1 monitoring system per monitored critical motor; channels depend on RTD/sensor count. | Optional | Yes | motor_count | Eight compressor motors => Qty 8 systems or channel groups | Can be grouped depending on product architecture.
QR_PQ_001 | PQ_CLASSA_001 | PF_PQ | Power Quality Recorder | PCC / bus / feeder count | Default: 1 PQ recorder per monitored PCC, bus, or feeder. | Strongly Recommended | Yes | pcc_count | One grid connection point => Qty 1 | Channel count and Class A requirement must be checked.
QR_DFR_001 | DFR_DDR_001 | PF_DFR | Digital Fault / Disturbance Recorder | Channel group / station / bus count | Quantity based on voltage/current channel count and monitored points. | Required | Yes | channel_count | One station with 16 current and 8 voltage channels => product/channel configuration | Channel count drives configuration.
QR_PMU_001 | PMU_001 | PF_PMU | Phasor Measurement Unit | Measurement point count | Default: 1 PMU per monitored bus/PCC/measurement point unless integrated with recorder. | Recommended | Yes | measurement_point_count | Two monitored buses => Qty 2 | Confirm standalone vs integrated PMU.
QR_SOFT_001 | SUB_SOFT_001 | PF_SOFTWARE | Monitoring Software / Asset Platform | Site / asset / tag / user count | Quantity/license depends on software licensing model. | Optional | Yes | asset_count_or_tag_count | Five substations with 200 assets => license TBD | Commercial team must confirm license model.
QR_GATEWAY_001 | COMM_SCADA_001 | PF_GATEWAY | Communication Gateway / Integration Module | Site / protocol boundary / network segment count | Quantity based on integration architecture and protocol conversion boundaries. | Optional | Yes | site_count_or_gateway_count | One Modbus-to-IEC61850 gateway per substation | May be accessory rather than BOQ line.

## 10_Compatibility_Rules
Compatibility Rules - Guardrails for Product Matching
Use these rules before AI-generated explanations. Product matching should be rules-first and AI-explained.
Rule ID | Rule Type | Scenario ID | Asset Type | Condition / Trigger | Recommended Action | Severity | Notes
CR_001 | Exclusion | TR_DGA_001 | Dry-type transformer | Asset type is dry-type transformer | Do not recommend oil DGA products; consider dry-type temperature monitoring if relevant. | High | Prevents false DGA recommendation.
CR_002 | Must-have | PQ_CLASSA_001 | PCC / bus / feeder | Customer explicitly requires Class A power quality | Only recommend products with confirmed Class A capability. | High | Do not downgrade unless approved.
CR_003 | Must-have | COMM_SCADA_001 | Monitoring system | Customer specifies IEC 61850 / DNP3 / Modbus | Check product protocol support or include gateway/interface accessory. | High | Flag protocol gaps.
CR_004 | Review | GIS_PD_001 | GIS | GIS bay count or layout is missing | Do not finalize GIS PD quantity; create missing information question. | High | Drawing dependency.
CR_005 | Review | BRK_HEALTH_001 | Circuit breaker | Breaker count is not clear from documents | Flag quantity as low-confidence and request SLD/equipment list. | Medium
CR_006 | Compatibility | TR_BUSH_001 | Transformer bushing | Bushing count or phase configuration is missing | Recommend candidate family but keep channel count TBD. | Medium
CR_007 | Compatibility | GEN_PD_001 | Generator | Asset type is motor rather than generator | Use motor monitoring product family instead of generator monitoring. | High | Avoid cross-asset mismatch.
CR_008 | Compatibility | MTR_PD_001 | Motor | Motor voltage/rating is not provided | Use generic motor monitoring candidate and flag missing rating. | Medium
CR_009 | Environmental | CAB_ENV_001 | Outdoor cabinet | Ambient temperature/humidity/IP rating is specified | Check product environmental rating or add enclosure/accessory requirement. | Medium | Can affect product configuration.
CR_010 | Quantity | DFR_DDR_001 | Substation / feeder | Voltage/current channel count is missing | Do not finalize recorder configuration; request channel list. | High | DFR/PQ quantity may depend on channels.
CR_011 | Quantity | PMU_001 | Grid measurement point | Measurement point count is missing | Ask for monitored buses/PCCs and time sync requirement. | Medium
CR_012 | Integration | SUB_SOFT_001 | Multi-asset / site | Software license model is not known | Keep software line as TBD and route to commercial/product owner. | Medium | Licensing is often commercial-specific.
CR_013 | Evidence | All | All | AI confidence below 0.70 | Mark as 'Needs Review' and do not use as must-have matching criterion. | High | Confidence threshold can be tuned.
CR_014 | Evidence | All | All | No evidence text is available | Do not accept extracted requirement; ask AI to cite source or mark as assumption. | High | Evidence is mandatory.

## 11_Input_Document_Index (hidden)
Input Document Index Template
Use this as the intake register for all customer-provided documents and drawings.
Project ID | Document ID | File Name | File Type | Source Channel | Received Date | Document Role | Version | Parsed Status | Notes
|  |  | Project Specification / Raw Email / Circuit Drawing / SLD / Equipment List / Tender / BOQ | Email / Upload / SharePoint / Salesforce |  | Primary / Supporting / Drawing / Commercial |  | Not Started / Parsed / Failed / Needs Review

## 12_Extracted_Evidence (hidden)
AI Output Template - Extracted Evidence
AI should extract evidence first. Every scenario or requirement should be traceable to evidence text and source location.
Project ID | Evidence ID | Source Document | Page / Location | Evidence Text | Related Scenario ID | Related Scenario | Asset Type | Asset Tag | Confidence | Extraction Notes

## 13_Structured_Requirements (hidden)
AI Output Template - Structured Requirements
AI should map raw customer requirements to Scenario ID and Metric ID. Avoid free-form parameter names when a standard metric exists.
Requirement ID | Project ID | Scenario ID | Scenario | Asset Type | Asset Tag | Metric ID | Metric Name | Parameter Value | Unit | Requirement Type | Evidence ID | Confidence | Missing / Assumption
Must-have / Preferred / Reference / Quantity Basis / Unknown

## 14_Drawing_Asset_List (hidden)
AI Output Template - Drawing / SLD Asset List
Do not calculate BOQ quantity directly from images. First convert drawings into this structured asset list.
Project ID | Drawing ID | Asset Tag | Asset Type | Voltage Level | Power / Rating | Quantity | Connected To | Monitoring Zone | Source Location | Confidence | Notes
Transformer / Circuit Breaker / GIS Bay / Generator / Motor / PCC / Bus / Feeder

## 15_Product_Matching_Output (hidden)
AI / Rules Output Template - Product Matching Result
Product matching should use Scenario ID + Asset Type + Metric/Parameter rules. AI can then explain the match reason.
Project ID | Requirement ID | Candidate Product ID | Candidate Model | Product Family ID | Product Family | Scenario Match | Asset Match | Parameter Match Result | Match Score | Match Status | Matched Parameters | Gap / Risk | Recommendation
[6 empty] | Yes / Partial / No | Yes / Partial / No | Matched / Partial / Not Matched / Missing Data |  | Recommended / Alternative / Not Recommended / Needs Review

## 16_Draft_BOQ (hidden)
Draft BOQ Output Template
Draft BOQ should always show quantity basis and assumptions. Final quotation requires human review.
Project ID | BOQ Line | Product ID | Product Model | Product Description | Related Scenario ID | Related Asset(s) | Quantity | Unit | Quantity Basis | Assumption | Confidence | Review Status | Notes
[8 empty] | set / pc / license / system |  |  |  | Draft / Needs Review / Approved / Rejected

## 17_Missing_Info_Questions (hidden)
Missing Information and Clarification Questions
Use this sheet to prevent the AI from guessing. Missing information should generate customer or engineer clarification questions.
Project ID | Missing Information Item | Related Scenario ID | Why It Matters | Suggested Customer / Engineer Question | Priority | Owner | Status | Notes
| Transformer oil type | TR_DGA_001 | Required to confirm DGA applicability and compatibility. | Please confirm whether the transformer uses mineral oil, ester oil, or another insulation fluid. | High | Sales / Product Engineer | Open
| Number of monitored transformers | TR_DGA_001; TR_TEMP_001 | Required for BOQ quantity. | Please confirm how many transformers are included in the monitoring scope. | High | Sales / Customer | Open
| Circuit breaker count | BRK_HEALTH_001 | Required for breaker monitor quantity. | Please provide the latest SLD or breaker equipment list. | High | Sales / Customer | Open
| GIS bay layout | GIS_PD_001 | Required for PD sensor placement and quantity. | Please provide GIS layout, bay list, or monitoring zone definition. | High | Product Engineer | Open
| Power quality class | PQ_CLASSA_001 | Determines whether Class A product capability is mandatory. | Please confirm whether Class A power quality compliance is required. | Medium | Sales / Customer | Open
| Communication protocol | COMM_SCADA_001 | Required for integration and gateway selection. | Please confirm required protocol: Modbus, DNP3, IEC 61850, IEC 60870, or other. | Medium | Customer IT / SCADA | Open
| Ambient temperature and humidity | CAB_ENV_001 | Required for enclosure and environmental suitability. | Please confirm site operating temperature and humidity range. | Medium | Customer / Engineer | Open
| Recorder channel list | DFR_DDR_001; PQ_CLASSA_001 | Required for DFR/PQ configuration and quantity. | Please provide voltage/current channel list and monitored feeders/buses. | High | Protection Engineer | Open

## 18_Review_Workflow (hidden)
Human Review Workflow
Recommended governance: AI generates draft evidence, requirements, matches, and BOQ; humans approve before final quotation.
Object Type | Review Step | Owner Role | Entry Criteria | Decision / Check | Output | SLA / Notes
Extracted Evidence | Evidence validation | Sales Engineer / Application Engineer | AI extracted scenario evidence | Is the evidence truly related to Qualitrol application? | Accepted / Rejected / Needs clarification | Reject unsupported evidence.
Structured Requirement | Metric normalization review | Product Engineer | Requirement mapped to Metric ID | Is the metric name, value, unit, and asset context correct? | Approved requirement table | High-risk requirements should be reviewed before matching.
Drawing Asset List | Asset count validation | Electrical Engineer | AI extracted assets from SLD/drawing | Are asset types, tags, voltage levels, and counts correct? | Approved asset list | Critical for quantity calculation.
Product Matching | Candidate product review | Product Owner / Application Engineer | Rules + AI matching output | Does the product family/model meet must-have requirements? | Recommended / Alternative / Not recommended | Product model data must be validated.
Draft BOQ | BOQ quantity review | Sales Engineer / Product Engineer | Draft BOQ generated with quantity basis | Are quantity, assumption, and accessories correct? | Final BOQ draft for quotation | Every line needs confidence and assumption.
Missing Info | Clarification closure | Sales / Customer / Engineer | Open missing information list | Can missing data be answered or should assumption be accepted? | Closed / Accepted assumption / Escalated | Do not finalize high-severity gaps.

## 19_Reference_Lists (hidden)
Reference Lists
Reference values for dropdowns or Power Automate/Dify validation logic.
List Name | Allowed Value | Description
Status | TBD | To be completed.
Status | Draft | Draft output generated by AI.
Status | Needs Review | Requires human review.
Status | Approved | Approved by responsible reviewer.
Status | Rejected | Rejected by responsible reviewer.
Status | Open | Clarification is open.
Status | Closed | Clarification is closed.
Priority | High | Critical to matching or BOQ quantity.
Priority | Medium | Useful for configuration or risk reduction.
Priority | Low | Optional or nice-to-have.
Requirement Type | Must-have | Must be met by product.
Requirement Type | Preferred | Preferred but not mandatory.
Requirement Type | Reference | Contextual information.
Requirement Type | Quantity Basis | Used to calculate quantity.
Requirement Type | Unknown | Cannot classify yet.
Match Status | Recommended | Best fit.
Match Status | Alternative | Possible but not primary.
Match Status | Not Recommended | Does not meet requirements.
Match Status | Needs Review | Requires engineer review.