## 03_Scenario_Master
Scenario Master - Controlled Scenario Taxonomy
Use Scenario ID as the stable key for AI extraction, product matching, quantity rules, and BOQ generation.
Scenario ID | Scenario Category | Application Scenario | Asset Type | Typical Metrics / Requirements | Common Evidence Keywords / Synonyms | Related Product Families | Quantity Basis | Drawing Dependency | Requirement Output Fields | Review Notes
| High-level grouping; used to group BOQ output. | Specific application; shown in outputs & matching. | Primary asset; drives asset matching. | Reference metrics; given to the extraction LLM as context. | ';'-separated keywords used to detect this scenario in text. | Reference only; real linkage comes from sheet 06. | Reference note; real quantity logic is in sheet 09. | Reference note; not enforced by code. | ';'-separated fields the LLM should output. | Human note; not used by the pipeline.
TR_DGA_001 | Transformer | Transformer dissolved gas monitoring | Oil-filled power transformer | DGA gas count; H2; CO; CO2; CH4; C2H2; C2H4; C2H6; O2/N2; moisture in oil; oil temperature | DGA; dissolved gas; gas-in-oil; online gas monitor; transformer oil analysis; hydrogen monitor; acetylene; oil chromatograph | DGA Monitor; Transformer Monitor; Asset Monitoring Software | 1 unit per monitored oil-filled transformer | Asset count from SLD or transformer list recommended | asset_tag; transformer_count; gas_count; oil_type; communication_protocol; alarm_threshold | Exclude dry-type transformers unless another non-DGA monitoring need exists.
TR_TEMP_001 | Transformer | Transformer oil and winding temperature monitoring | Power transformer / distribution transformer | Top oil temperature; winding temperature; hot-spot temperature; ambient temperature; cooling stage; load current | oil temp; winding temp; hot spot; temperature indicator; thermal monitor; cooling control; fan control | Transformer Temperature Monitor; Cooling Control; Transformer Monitor | 1 monitor per transformer or per transformer control cabinet | Asset count required; drawing useful but not mandatory | asset_tag; temperature_points; cooling_stage; ambient_range; alarm_setpoints | Confirm whether winding temperature is simulated, direct fiber, or RTD-based.
TR_BUSH_001 | Transformer | Transformer bushing condition monitoring | Transformer bushing | Capacitance; tan delta / power factor; leakage current; phase angle; voltage level; bushing count | bushing monitor; tan delta; capacitance; power factor; leakage current; high-voltage bushing | Bushing Monitor; Transformer Monitor; Asset Monitoring Software | Typically one monitoring set per transformer; channel count depends on bushing/phase count | Drawing or bushing list required for accurate channel count | asset_tag; bushing_count; phase_count; voltage_level; reference_voltage; alarm_threshold | Quantity may depend on three-phase/six-bushing configuration.
TR_PD_001 | Transformer | Transformer partial discharge monitoring | Power transformer | PD magnitude; PD location; UHF/HFCT/acoustic sensor count; voltage level; alarm threshold | partial discharge; PD; UHF; HFCT; acoustic; insulation defect; discharge monitoring | Partial Discharge Monitor; Transformer Monitor; PD Sensors | Sensor and monitor count depends on transformer design and monitoring zones | Drawing/engineering review recommended | asset_tag; sensor_type; sensor_count; voltage_level; monitoring_zone; alarm_threshold | Requires product engineer review for sensor placement.
TR_AUX_001 | Transformer | Transformer auxiliary protection and indication | Oil-filled transformer | Pressure relief; oil level; oil flow; Buchholz relay; temperature contacts; alarm/trip contacts | pressure relief; PRD; oil level; oil flow; Buchholz; relay; sudden pressure; alarm contacts | Sensors; Pressure Relief Device; Oil Level Indicator; Flow Indicator; Buchholz Relay | Quantity depends on transformer accessories and protection points | Asset accessory list required | asset_tag; accessory_type; contact_type; mounting; alarm_or_trip | Often OEM or replacement accessory opportunity.
DRY_TR_TEMP_001 | Transformer | Dry-type transformer temperature monitoring | Dry-type transformer | Winding temperature; ambient temperature; fan control; alarm/trip contacts; enclosure temperature | dry transformer; cast resin; winding temperature; fan control; temperature relay | Dry-Type Transformer Temperature Monitor | 1 monitor per dry-type transformer | Asset count required | asset_tag; winding_temperature_points; fan_control; alarm_contacts; ambient_range | DGA is not applicable to dry-type transformer.
BRK_HEALTH_001 | Breaker | Circuit breaker health monitoring | High-voltage / medium-voltage circuit breaker | Trip time; close time; coil current; operation count; contact wear; SF6 pressure/density; motor current | breaker monitor; trip coil; close coil; operating time; mechanism timing; SF6 density; CBM; circuit breaker diagnostics | Breaker Monitor; Switchgear Monitor; Asset Monitoring Software | 1 monitor per breaker; channel count depends on auxiliary contacts and mechanism points | Breaker count from SLD or switchgear list required | asset_tag; breaker_count; voltage_level; operating_mechanism; coil_voltage; sf6_required | Confirm breaker type and whether SF6 measurements are needed.
GIS_PD_001 | GIS | GIS partial discharge monitoring | Gas-insulated switchgear / GIS bay | PD signal; UHF sensor count; bay count; compartment count; voltage level; monitoring zone | GIS PD; UHF; gas insulated switchgear; GIS bay; partial discharge; switchgear insulation | GIS PD Monitor; UHF Sensor; PD Monitoring Software | Quantity based on GIS bay count, compartments, or monitoring zones | GIS layout/drawing strongly required | gis_bay_count; compartments; sensor_count; voltage_level; monitoring_zone; alarm_threshold | Avoid estimating sensor count without layout.
SWG_PD_001 | Switchgear | MV switchgear partial discharge monitoring | Medium-voltage switchgear / cable termination | PD level; HFCT/TEV/UHF sensor type; feeder count; cable termination count; voltage level | MV PD; switchgear PD; TEV; HFCT; cable termination; feeder insulation | Partial Discharge Monitor; Switchgear PD Sensors | Quantity based on switchgear panels/feeders/monitoring zones | Switchgear lineup drawing required for accuracy | panel_count; feeder_count; sensor_type; voltage_level; monitoring_zone | Panel-level or feeder-level scope must be confirmed.
GEN_PD_001 | Generator | Generator stator partial discharge monitoring | Generator | PD level; generator voltage; MW/MVA rating; stator winding; coupler count; online/offline mode | generator PD; stator PD; Iris Power; winding insulation; coupler; rotating machine PD | Generator PD Monitor; Iris Power Sensors; Generator Monitoring Software | Typically per generator unit; sensor/coupler count depends on generator design | Generator list required; design review recommended | generator_tag; voltage_level; rating_mva; sensor_count; online_mode; alarm_threshold | Large rotating machine expertise required.
GEN_EWV_001 | Generator | Generator end-winding vibration monitoring | Turbine generator / large generator | End-winding vibration; acceleration; frequency; sensor count; location; alarm threshold | end winding vibration; EWV; stator end winding; vibration sensor; generator vibration | End-Winding Vibration Monitor; Generator Monitoring Platform | Per generator unit; sensor count based on winding locations | Engineering design required | generator_tag; sensor_count; vibration_threshold; mounting_location; speed | Not every generator requires this; scope driven by risk and asset criticality.
GEN_AIRGAP_001 | Generator | Hydro generator air gap and rotor flux monitoring | Hydro generator / pumped storage generator | Air gap; rotor flux; eccentricity; pole count; speed; sensor count | air gap; rotor flux; eccentricity; hydro generator; pole flux; rotor monitoring | Air Gap Monitor; Rotor Flux Monitor; Generator Monitoring Software | Per generator unit; sensor count depends on generator design | Generator design and unit count required | generator_tag; unit_count; pole_count; sensor_count; speed; alarm_threshold | Strong use case for hydro and pumped storage.
MTR_PD_001 | Motor | Large motor insulation monitoring | Large MV/HV motor | PD level; motor voltage; motor rating; stator insulation condition; coupler/sensor count | motor PD; stator insulation; Iris Power motor; MV motor; HV motor; coupler | Motor PD Monitor; Motor Monitoring Platform | Per monitored motor; sensors depend on motor design | Motor list required | motor_tag; rating_kw; voltage_level; sensor_count; online_mode | Prioritize critical motors such as compressors, pumps, fans, mills.
MTR_TEMP_001 | Motor | Large motor thermal and condition monitoring | Large motor | RTD temperature; bearing temperature; load current; operating hours; vibration if applicable | motor temperature; RTD; bearing temperature; winding temperature; motor monitor; reliability | Motor Monitor; Temperature Monitor; Asset Monitoring Software | Per monitored motor; channel count depends on RTD/bearing points | Motor list and I/O point list required | motor_tag; rtd_count; bearing_points; current; alarm_threshold | Clarify whether vibration is in scope or handled by another system.
PQ_CLASSA_001 | Grid / Power Quality | Class A power quality monitoring | PCC, bus, feeder, grid connection point | Class A compliance; harmonics; flicker; voltage sag/swell; frequency; unbalance; transient; sampling rate | Class A PQ; power quality; harmonics; flicker; sag; swell; EN 50160; IEC 61000; PQ recorder | Power Quality Recorder; Disturbance Recorder; Monitoring Software | Typically 1 unit per PCC/bus/monitored feeder | SLD strongly recommended to identify PCCs and feeders | pcc_count; voltage_level; current_channels; pq_class; standard; time_sync | Do not recommend non-Class A product when Class A is explicitly required.
DFR_DDR_001 | Grid / Disturbance | Digital fault and disturbance recording | Substation bus, feeder, generator connection, PCC | Voltage/current channels; sampling rate; trigger logic; event recording; time sync; sequence of events | DFR; DDR; disturbance recorder; fault recorder; transient recorder; event recorder; fault analysis | Digital Fault Recorder; Disturbance Recorder; Monitoring Software | 1 unit per station/bus or per channel group depending on scope | SLD and channel list required | channel_count; voltage_channels; current_channels; sampling_rate; trigger; time_sync | Channel count is the critical quantity driver.
PMU_001 | Grid / Synchrophasor | Phasor measurement and wide-area monitoring | Transmission grid, PCC, generator interconnection | Synchrophasor; timestamp accuracy; reporting rate; voltage/current channels; PTP/GPS time sync | PMU; synchrophasor; phasor measurement; wide-area monitoring; WAMS; IEEE C37.118 | PMU; Disturbance Recorder; Grid Monitoring Software | 1 unit per monitored bus/PCC/measurement point | SLD and grid measurement points required | measurement_point_count; reporting_rate; time_sync; standard; channel_count | Often driven by grid operator requirements.
FAULT_LOC_001 | Grid / Fault Location | Transmission line fault location | Transmission line / feeder | Line length; voltage level; current/voltage channels; fault type; GPS time sync | fault locator; line fault; distance to fault; travelling wave; transmission line | Fault Location System; DFR; Grid Monitoring Software; PF_TWS | Per line or monitored terminal depending on topology | Line diagram and terminal list required | line_count; terminal_count; voltage_level; time_sync; line_length | Quantity depends on single-ended or multi-ended solution.
SUB_SOFT_001 | Software / Platform | Substation or fleet asset monitoring software | Multi-asset substation / fleet | Asset count; data points; protocols; alarm rules; dashboards; historian/SCADA integration | asset management; monitoring software; dashboard; SCADA; Modbus; IEC 61850; DNP3; historian | Asset Monitoring Software; SmartSub / Monitoring Platform | Per site, per asset, or per software license model | Documented site scope and integration points required | site_count; asset_count; protocol; tag_count; user_count; license_model | License model must be confirmed with product/commercial team.
CAB_ENV_001 | Environment | Cabinet or substation environmental monitoring | Monitoring cabinet, control room, outdoor enclosure | Ambient temperature; humidity; enclosure rating; IP/NEMA rating; heater/fan; condensation | ambient temperature; humidity; RH; IP rating; enclosure; condensation; cabinet heater; outdoor environment | Environmental Sensors; Cabinet Accessories; Monitoring Platform | Per cabinet/enclosure or per monitoring zone | Cabinet count required | cabinet_count; ambient_range; humidity_range; enclosure_rating; power_supply | Useful as supporting requirements for product selection.
COMM_SCADA_001 | Integration | SCADA and communication integration | Monitoring system / site integration | Modbus; DNP3; IEC 61850; IEC 60870; Ethernet; fiber; serial; cybersecurity; time sync | SCADA; protocol; Modbus; DNP3; IEC 61850; Ethernet; integration; gateway; API | Gateway; Monitoring Software; Communication Module | Usually per site/system; module count depends on architecture | Integration architecture required | protocol; network_type; cybersecurity; time_sync; gateway_required | This scenario may not create a stand-alone BOQ line but affects product selection.
FMS_001 | Grid / Disturbance | Centralized fault management system and DFR data platform | Multi-DFR substation / substation network server | Server count; iQ+ license count; managed device count; communication network | FMS; fault management system; iQ+; iQ plus; master station; CASHEL FMS; centralized recording; central server; substation data server; DFR master station; iQ master station; data management platform; rackmount server; network server | PF_DFR; PF_TWS; PF_PMU; PF_SOFTWARE | 1 server system per site; additional client workstation licenses per operator | Network device inventory and site topology helpful | server_count; managed_device_count; site_count; client_count | Always paired with 2+ IDM+/TWS deployments. iQ+ Master Station is the standard software.
GIS_ARC_001 | GIS | GIS arc flash detection and localization | Gas-insulated switchgear / GIS compartment | Arc event count; arc location; gas compartment; UHF signal level; flashover | arc detection; arc flash; arc localization; GIS arc; flashover; GIS flashover; arc discharge; flashover detection; arc fault detection; arc event | PF_GIS_PD | No additional hardware; feature of PDMG-RH Gen3 (uses existing UHF sensors) | GIS layout and compartment list required for localization | gis_bay_count; arc_detection_option; compartment_list | Arc Detection is an add-on feature of PDMG-RH Gen3. No extra hardware needed. Only quote if PDMG-RH Gen3 is already in scope.
WAMS_001 | Grid / Synchrophasor | Wide area monitoring system for multi-site grid stability | Multi-substation transmission grid / phasor data concentrator | PMU count; phasor data concentrator count; reporting rate; GPS latency; site count | WAMS; wide area monitoring; wide area measurement system; PDC; phasor data concentrator; real-time oscillation monitoring; power swing monitoring; inter-area oscillation; grid stability monitoring; frequency monitoring; voltage angle | PF_PMU; PF_SOFTWARE | 1 PMU per monitored grid measurement point; 1 PDC per substation cluster | Grid topology and SLD required; multi-site coordination | pmu_count; site_count; grid_segment; reporting_rate | Typically integrated with GCCIA or national SCADA. PMU_001 is per-device; WAMS_001 covers the system-wide wide-area network use case.

## 04_Metric_Dictionary
Metric Dictionary - Standard Parameter Names and Units
Map customer raw terms to these standard metrics before product matching. This avoids uncontrolled AI-generated parameter names.
Metric ID | Standard Metric Name | Synonyms / Raw Terms | Standard Unit | Data Type | Applies To | Used For | Example Values | Required for Matching | Normalization Notes
| Canonical metric name used in matching & outputs. | ';'-separated customer terms mapped to this metric. | Canonical unit; used in prompts/outputs. | integer/float/text/list; controls value parsing in Step 1. | Assets/scenarios this metric applies to (prompt context). | Reference note; not used by the pipeline. | Reference only; NOT read by the pipeline. | Yes/No; flags a must-have metric in Step 1. | Human note; not used by the pipeline.
MET_ASSET_COUNT | Asset Count | quantity; qty; number of assets; equipment count | count | integer | All assets | Quantity calculation | 2 transformers; 6 breakers | Yes | Usually extracted from drawing asset list or equipment list.
MET_ASSET_TAG | Asset Tag | tag; equipment ID; device name; transformer name; breaker ID | text | text | All assets | Evidence linking and BOQ basis | T1; T2; CB-101 | Yes | Preserve original tag exactly.
MET_ASSET_TYPE | Asset Type | equipment type; device type; asset class | text | controlled text | All assets | Scenario and product filtering | Transformer; GIS; Circuit Breaker | Yes | Map to controlled asset type values.
MET_VOLTAGE_LEVEL | Voltage Level | rated voltage; system voltage; nominal voltage; kV level | kV | number/range | Transformer; GIS; Breaker; Grid; Motor; Generator | Compatibility and engineering scope | 33 kV; 110 kV; 220 kV | Yes | Normalize all voltage values to kV.
MET_POWER_RATING | Power Rating | MVA; MW; kW; rated power; apparent power | MVA/MW/kW | number | Transformer; Generator; Motor | Sizing and priority | 100 MVA; 500 MW; 2 MW | Preferred | Keep original unit and normalized unit if possible.
MET_CURRENT_CHANNELS | Current Channels | CT inputs; current inputs; current channels | count | integer | DFR; PQ; PMU; Breaker | Channel count and product configuration | 4; 8; 16 | Yes for recorders | Count physical measurement channels.
MET_VOLTAGE_CHANNELS | Voltage Channels | VT inputs; voltage inputs; voltage channels | count | integer | DFR; PQ; PMU | Channel count and product configuration | 3; 4; 8 | Yes for recorders | Count physical measurement channels.
MET_PQ_CLASS | Power Quality Class | Class A; PQ class; IEC 61000-4-30 class | text | controlled text | Power Quality | Product eligibility | Class A; Class S | Yes when specified | If Class A is specified, lower class should be excluded.
MET_HARMONICS | Harmonics Requirement | THD; harmonic; interharmonic; harmonic measurement | % / order | text/number | Power Quality; Industrial | PQ product capability | up to 50th order; THD < 5% | Preferred | Keep both measurement range and limit if stated.
MET_FLICKER | Flicker Requirement | Pst; Plt; flicker | text/number | text/number | Power Quality | PQ product capability | Pst/Plt required | Preferred | Map to PQ capability.
MET_SAG_SWELL | Sag / Swell Recording | voltage sag; voltage dip; voltage swell; RMS variation | text | boolean/text | Power Quality; DFR | Event recording capability | required; threshold 90% | Preferred | If threshold is provided, retain it.
MET_SAMPLING_RATE | Sampling Rate | sample rate; sampling frequency; waveform sampling | samples/cycle or Hz | number/text | DFR; PQ; PMU | Recorder selection | 256 samples/cycle; 10 kHz | Preferred | Normalize carefully; retain original phrase.
MET_TIME_SYNC | Time Synchronization | GPS; IRIG-B; PTP; NTP; time sync; timestamp accuracy | text | controlled text | DFR; PQ; PMU; Grid Monitoring | System integration | GPS; IRIG-B; PTP | Preferred | Important for event correlation.
MET_REPORTING_RATE | Reporting Rate | PMU rate; frames per second; reporting frequency | fps / Hz | number | PMU | PMU compliance | 25 fps; 50 fps; 60 fps | Preferred | Normalize to frames per second if possible.
MET_DGA_GAS_COUNT | DGA Gas Count | number of gases; gas channels; 5-gas; 9-gas; multi-gas | count | integer | Transformer DGA | Product selection | 1; 5; 9 | Yes for DGA | Map 'multi-gas' to unknown unless exact count is given.
MET_DGA_GAS_SPECIES | DGA Gas Species | H2; CO; CO2; CH4; C2H2; C2H4; C2H6; O2; N2 | text | list | Transformer DGA | Product capability matching | H2, CO, C2H2 | Preferred | Extract individual gas names if provided.
MET_MOISTURE_OIL | Moisture in Oil | water in oil; moisture; ppm water; relative saturation | ppm / %RS | number | Transformer | Transformer condition monitoring | 10 ppm; 20% RS | Preferred | Keep ppm and relative saturation separate.
MET_OIL_TEMPERATURE | Oil Temperature | top oil temp; oil temp; transformer oil temperature | °C | number/range | Transformer | Temperature monitoring and DGA correction | 95°C; -20 to 70°C ambient | Preferred | Differentiate oil temperature from ambient temperature.
MET_WINDING_TEMP | Winding Temperature | winding temp; hot-spot; hotspot temperature | °C | number/range | Transformer; Motor; Generator | Thermal monitoring | 120°C | Preferred | Map transformer and motor contexts separately.
MET_AMBIENT_TEMP | Ambient Temperature | site temperature; operating temperature; environment temperature | °C | range | All equipment / Enclosure | Environmental suitability | -20 to 70°C | Preferred | Do not confuse with asset operating temperature.
MET_HUMIDITY | Humidity | RH; relative humidity; moisture; ambient humidity | %RH | range/number | Cabinet; Environment; Site | Environmental suitability | 95% RH non-condensing | Preferred | Retain condensation condition.
MET_ENCLOSURE_RATING | Enclosure Rating | IP rating; NEMA; outdoor enclosure; cabinet rating | text | controlled text | Cabinet; Monitoring Device | Hardware configuration | IP54; IP65; NEMA 4X | Preferred | Keep IP and NEMA as text.
MET_PROTOCOL | Communication Protocol | SCADA; Modbus; DNP3; IEC 61850; IEC 60870; protocol | text | list | All monitoring systems | Integration and product selection | Modbus TCP; DNP3; IEC 61850 | Yes if specified | Multiple protocols may be required.
MET_NETWORK | Network Interface | Ethernet; serial; RS485; fiber; wireless | text | list | All monitoring systems | Integration and accessory selection | Ethernet; RS485; fiber optic | Preferred | Useful for gateways and accessories.
MET_POWER_SUPPLY | Power Supply | auxiliary supply; control power; AC/DC supply | V AC/DC | text/number | All devices | Hardware configuration | 110 VDC; 220 VAC | Preferred | Retain AC/DC.
MET_CONTACT_TYPE | Contact Type | alarm contact; trip contact; relay contact; dry contact | text | controlled text | Sensors; Protection accessories | I/O configuration | NO/NC; alarm; trip | Preferred | Map to I/O requirements.
MET_ALARM_THRESHOLD | Alarm Threshold | alarm; warning; trip threshold; setpoint | varies | number/text | All monitoring | Configuration and acceptance | H2 alarm 100 ppm; temp alarm 95°C | Preferred | Attach threshold to the relevant metric.
MET_PD_LEVEL | Partial Discharge Level | PD magnitude; apparent charge; discharge level | pC / mV / dB | number/text | Transformer; GIS; Switchgear; Generator; Motor | PD monitoring requirement | 500 pC; warning level TBD | Preferred | Units vary by PD method; retain original unit.
MET_SENSOR_TYPE | Sensor Type | UHF; HFCT; TEV; acoustic; coupler; RTD | text | controlled text | PD; Temperature; Generator; Motor | Sensor selection | UHF; HFCT; RTD | Preferred | Map to product/sensor family.
MET_SENSOR_COUNT | Sensor Count | number of sensors; channels; couplers; probes | count | integer | All monitoring | Quantity and configuration | 3 sensors; 6 couplers | Yes when specified | May be calculated from asset count if not specified.
MET_BUSHING_COUNT | Bushing Count | number of bushings; HV bushings; phase bushings | count | integer | Transformer Bushing | Channel count and quantity | 3; 6 | Yes for bushing monitoring | Use bushing list/drawing for final quantity.
MET_CAPACITANCE | Bushing Capacitance | capacitance; C1; C2 | pF / nF | number | Transformer Bushing | Bushing monitoring | 500 pF | Preferred | May not be available in early-stage specs.
MET_TAN_DELTA | Tan Delta / Power Factor | tan delta; dielectric loss; power factor | % / decimal | number | Transformer Bushing | Bushing condition monitoring | 0.5%; 0.005 | Preferred | Normalize % vs decimal carefully.
MET_BREAKER_COUNT | Breaker Count | number of breakers; CB count; circuit breaker quantity | count | integer | Circuit Breaker | BOQ quantity | 6 breakers | Yes for breaker monitoring | Prefer SLD-derived count.
MET_TRIP_CLOSE_TIME | Trip / Close Time | opening time; closing time; trip time; close time | ms | number | Circuit Breaker | Breaker health monitoring | 40 ms; 60 ms | Preferred | May be an acceptance value or measured value.
MET_COIL_CURRENT | Coil Current | trip coil current; close coil current; coil signature | A | number | Circuit Breaker | Breaker mechanism diagnostics | 2.5 A | Preferred | Usually capability requirement rather than product filtering.
MET_SF6_PRESSURE | SF6 Pressure / Density | SF6; gas density; pressure; density relay | bar / MPa / density | number/text | GIS; Circuit Breaker | Gas monitoring scope | 0.5 MPa; density monitor required | Preferred | Only applicable to SF6 assets.
MET_GIS_BAY_COUNT | GIS Bay Count | bay count; GIS bays; compartments; feeders | count | integer | GIS | BOQ quantity | 8 bays | Yes for GIS PD | Prefer GIS layout.
MET_PANEL_COUNT | Switchgear Panel Count | switchgear panels; cubicles; feeders; cells | count | integer | MV Switchgear | BOQ quantity | 12 panels | Yes for switchgear PD | Panel vs feeder count must be distinguished.
MET_GENERATOR_COUNT | Generator Count | number of units; generator units; turbine units | count | integer | Generator | BOQ quantity | 4 units | Yes for generator monitoring | Extract unit number and tag.
MET_AIR_GAP | Air Gap | airgap; rotor-stator gap; eccentricity | mm / % | number | Hydro Generator | Air gap monitoring | 12 mm | Preferred | Often configuration/monitoring metric.
MET_ROTOR_FLUX | Rotor Flux | pole flux; flux probe; rotor flux | text/relative | number/text | Generator | Rotor monitoring | required; pole flux trend | Preferred | Exact units may vary by system.
MET_VIBRATION | Vibration | end winding vibration; bearing vibration; acceleration | mm/s / g / μm | number/text | Generator; Motor | Condition monitoring | 5 mm/s; 2 g | Preferred | Associate with location and axis if available.
MET_MOTOR_COUNT | Motor Count | number of motors; critical motors; pump motors; compressor motors | count | integer | Motor | BOQ quantity | 8 motors | Yes for motor monitoring | Use equipment list for final count.
MET_MOTOR_RTD_COUNT | Motor RTD Count | RTDs; temperature channels; winding RTDs; bearing RTDs | count | integer | Motor | Channel count | 6 winding RTDs; 2 bearing RTDs | Preferred | Required for temperature channel configuration.
MET_LICENSE_SCOPE | Software License Scope | site license; asset license; tag count; user count; software license | text/count | text/integer | Software | Commercial configuration | 100 tags; 5 users; site license | Preferred | Must be confirmed by product/commercial team.
MET_FEEDER_COUNT | Feeder / Circuit Count | feeder count; feeder; number of feeders; bay count; circuit count; number of circuits; feeders per panel; protected feeders; monitored feeders | count | integer | DFR; PQ; PMU; TWS | DFR model selection (determines analog channel count needed); TWS line module count | 6 feeders; 12 bays | Yes (for DFR/TWS sizing) | 1 feeder = typically 3 current + 1-3 voltage channels for full DFR coverage.
MET_LINE_COUNT | Transmission Line Count | line count; number of lines; transmission lines; monitored lines; line ends; circuits | count | integer | TWS; DFR | TWS FL module selection (FL-8 = 2/4/6/8 lines; FL-1 = 1 line) | 4 transmission lines; 2 line ends | Yes (for TWS) | TWS FL-8 starts with 2-line module, expandable to 8 in steps of 2.
MET_ANALOG_CHANNELS | Total Analog Channel Count | analog channels; AI count; analog inputs; channel count; total channels; number of analog; A/D channels; recording channels | count | integer | DFR; PQ; PMU; INFORMA PMD-A | IDM+ model/variant selection (9, 18, or 36 analog channels) | 9 analog channels; 18 AI; 36A | Yes (for DFR model selection) | IDM+ 9=9A/32D, IDM+ 18=18A/64D, IDM+ 36=36A/128D. Rule of thumb: 3 current + 3 voltage per feeder = 6 channels/feeder.
MET_DFR_FUNCTIONS | Required DFR / Recorder Functions | DFR functions; recording functions; monitoring options; PMU option; TWS option; Class A PQ option; SOE option; multifunctional recorder | text | controlled text (multi-select) | DFR; PMU; TWS | Determines which optional functions to order with IDM+: PMU, TWS card, Class A PQ | DFR + PMU; DFR + TWS + PMU; full functions | Yes (where stated) | IDM+ base = DFR+DDR. Options: +PMU (IEEE C37.118), +TWS card (±60m FL), +Class A PQ (IEC 61000-4-30 Class A).
MET_GPS_SYNC_ACCURACY | GPS Time Sync Accuracy | GPS accuracy; time tagging accuracy; timestamp accuracy; GPS time reference; time synchronization accuracy; 1PPS accuracy; IRIG-B accuracy | ns | number | TWS; PMU; DFR | Verify GPS accuracy meets double-ended TWS requirement (100 ns) and PMU C37.118 | 100 ns GPS; 1 µs IRIG-B | Yes (for TWS double-ended) | TWS double-ended requires GPS 100 ns. IDM+ GPS input provides 100 ns tagging.
MET_DIELECTRIC_STRENGTH | Dielectric Strength | dielectric strength; dielectric isolation | kV | number | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_MOUNTING_TYPE | Mounting Type | mounting type; mounting; mounting style; mounting orientation | text | controlled text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_PROCESS_CONNECTION | Process / Tank Connection | tank connection; tank connection thread; mounting thread; electrical connection type; process connection | text | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_DIAL_DIAMETER | Dial Diameter | dial diameter | mm | number | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_DIAL_RANGE | Dial / Measurement Range | dial range | text | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_SWITCH_RATING_AC | Switch Contact Rating (AC) | switch rating ac | text | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_SWITCH_RATING_DC | Switch Contact Rating (DC) | switch rating dc; switch dc rating | text | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_SWITCH_CONTACT_RATING | Switch Contact Rating | switch rating; switch contact rating | text | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_NUMBER_OF_SWITCHES | Number of Switches | number of switches | count | integer | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_INDICATION_ACCURACY | Indication / Measurement Accuracy | indication accuracy; measurement accuracy; input accuracy; switching accuracy; full range accuracy; accuracy | % | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_REPEATABILITY | Repeatability | repeatability | % | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_MAX_LOAD | Maximum Load | max load | text | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_POWER_CONSUMPTION | Power Consumption | power consumption | W / VA | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_FREQUENCY_BANDWIDTH | Frequency Bandwidth | frequency bandwidth; bandwidth | Hz | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_FLOAT_MECHANISM | Float Mechanism / Material | float mechanism; float material | text | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_ANALOG_OUTPUT | Analog Output Signal | analog output signal | text | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_RESPONSE_TIME | Response / Acquisition Time | response time; data acquisition time | s | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_WEIGHT | Weight | weight | kg | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_PROBE_LENGTH | Probe / Sensor Length | probe length | m / mm | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_CASE_MATERIAL | Case / Housing Material | case material | text | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_OPERATING_PRESSURE | Operating Pressure | operating pressure; oil inlet pressure | bar / psi | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_FLOW_RATE | Flow Rate | flow rate | text | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_PHASE_WINDOWS | Phase / Measurement Windows | phase windows | count | integer | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).
MET_STORAGE_TEMP | Storage Temperature | storage temperature | °C | text | Various products | Product parameter matching |  | No | Added from datasheet extraction (Step 0b).

## 05_Synonym_Mapping
Synonym Mapping - Raw Customer Terms to Scenario and Metric IDs
This sheet can be expanded over time with real customer document expressions. It supports both keyword and semantic matching.
Raw Term / Phrase | Mapped Scenario ID | Mapped Metric ID | Mapped Standard Meaning | Asset Context | Mapping Priority | Notes
| Scenario this term maps to (must exist in sheet 03). | Optional metric this term maps to (sheet 04). | Human-readable meaning; reference only. | Fallback asset type when scenario has none. | High/Medium/Low; converted to match confidence. | Human note; not used by the pipeline.
online oil gas analysis | TR_DGA_001 | MET_DGA_GAS_SPECIES | Transformer dissolved gas monitoring | Transformer | High | Strong DGA evidence.
oil chromatograph | TR_DGA_001 | MET_DGA_GAS_COUNT | DGA monitor requirement | Transformer | High | May imply multi-gas DGA.
hydrogen monitor | TR_DGA_001 | MET_DGA_GAS_SPECIES | Hydrogen gas monitoring in transformer oil | Transformer | Medium | Could be single-gas DGA; confirm gas count.
top oil temperature | TR_TEMP_001 | MET_OIL_TEMPERATURE | Transformer oil temperature | Transformer | High
hot spot temperature | TR_TEMP_001 | MET_WINDING_TEMP | Transformer winding hot-spot temperature | Transformer | High
bushing tan delta | TR_BUSH_001 | MET_TAN_DELTA | Transformer bushing condition monitoring | Transformer bushing | High
bushing capacitance | TR_BUSH_001 | MET_CAPACITANCE | Transformer bushing capacitance monitoring | Transformer bushing | High
breaker timing | BRK_HEALTH_001 | MET_TRIP_CLOSE_TIME | Circuit breaker mechanism timing | Circuit breaker | High
trip coil current | BRK_HEALTH_001 | MET_COIL_CURRENT | Breaker trip coil current signature | Circuit breaker | High
SF6 density | BRK_HEALTH_001 | MET_SF6_PRESSURE | Gas density/pressure monitoring | Circuit breaker / GIS | Medium | Check whether asset is breaker or GIS.
GIS UHF | GIS_PD_001 | MET_SENSOR_TYPE | GIS partial discharge monitoring | GIS | High
TEV sensor | SWG_PD_001 | MET_SENSOR_TYPE | MV switchgear PD sensor | Switchgear | Medium | May also appear in cable/switchgear PD scope.
HFCT | SWG_PD_001 | MET_SENSOR_TYPE | HFCT sensor for PD/current path monitoring | Switchgear / Cable / Transformer | Medium | Need asset context.
stator PD | GEN_PD_001 | MET_PD_LEVEL | Generator stator partial discharge monitoring | Generator | High
Iris Power | GEN_PD_001 | MET_PD_LEVEL | Generator or motor monitoring product clue | Generator / Motor | Medium | Use asset context to distinguish generator vs motor.
end winding vibration | GEN_EWV_001 | MET_VIBRATION | Generator end-winding vibration monitoring | Generator | High
air gap | GEN_AIRGAP_001 | MET_AIR_GAP | Hydro generator air gap monitoring | Hydro generator | High
rotor flux | GEN_AIRGAP_001 | MET_ROTOR_FLUX | Generator rotor flux monitoring | Generator | High
Class A PQ | PQ_CLASSA_001 | MET_PQ_CLASS | Class A power quality monitoring | Grid / PCC | High
harmonic analysis | PQ_CLASSA_001 | MET_HARMONICS | Power quality harmonics monitoring | Grid / Industrial | Medium | Confirm if recorder requirement or study only.
fault recorder | DFR_DDR_001 | MET_SAMPLING_RATE | Digital fault recording | Substation / Feeder | High
disturbance recorder | DFR_DDR_001 | MET_SAMPLING_RATE | Digital disturbance recording | Grid / Plant | High
PMU | PMU_001 | MET_REPORTING_RATE | Phasor measurement | Grid / PCC | High
synchrophasor | PMU_001 | MET_REPORTING_RATE | Synchrophasor measurement | Grid | High
Modbus TCP | COMM_SCADA_001 | MET_PROTOCOL | Communication protocol | All monitoring systems | High
IEC 61850 | COMM_SCADA_001 | MET_PROTOCOL | Substation communication protocol | Substation systems | High
IP65 | CAB_ENV_001 | MET_ENCLOSURE_RATING | Enclosure rating | Cabinet / outdoor device | Medium
95% RH | CAB_ENV_001 | MET_HUMIDITY | Operating humidity | Environment | Medium
TWS | FAULT_LOC_001 |  | Traveling Wave System (fault locator) | Transmission line | High | Abbreviation used in Qualitrol/Hathaway product line; word-boundary matched.
traveling wave system | FAULT_LOC_001 |  | Traveling wave fault location system | Transmission line | High | Full product category name.
travelling wave system | FAULT_LOC_001 |  | Travelling wave fault location system (UK sp.) | Transmission line | High | UK spelling variant.
traveling wave fault | FAULT_LOC_001 |  | Traveling wave fault location method | Transmission line | High | Common phrase in specifications.
travelling wave | FAULT_LOC_001 |  | Travelling wave fault location | Transmission line | Medium | Shorter form; may appear in protection specs.
fault locator | FAULT_LOC_001 |  | Transmission line fault locator device | Transmission line | High | Generic device name.
line fault location | FAULT_LOC_001 |  | Transmission line fault location | Transmission line | High | Common spec phrase.
distance to fault | FAULT_LOC_001 |  | Fault distance measurement on transmission line | Transmission line | High | Measurement output of fault locator.
TWS FL | FAULT_LOC_001 |  | Qualitrol TWS FL-series product reference | Transmission line | High | Matches TWS FL-2 and other FL models.
TWFL | FAULT_LOC_001 |  | Traveling Wave Fault Locator acronym | Transmission line | High | Acronym form.
transmission line fault | FAULT_LOC_001 |  | Fault on transmission line | Transmission line | Medium | May appear in protection relay specs.
single-ended fault location | FAULT_LOC_001 |  | Single-ended traveling wave fault location | Transmission line | High | Single-end TWS method.
double-ended fault location | FAULT_LOC_001 |  | Double-ended traveling wave fault location | Transmission line | High | Double-end GPS-sync TWS method.
IDM+ | DFR_DDR_001; PMU_001; FAULT_LOC_001; PQ_CLASSA_001 | MET_SAMPLING_RATE | Qualitrol IDM+ multifunction recorder (DFR/DDR/PMU/TWS/PQ) | Substation / feeder | High
IDM plus | DFR_DDR_001 |  | Qualitrol IDM+ multifunction recorder | Substation / feeder | High
IDM | DFR_DDR_001 | MET_SAMPLING_RATE | Qualitrol IDM/IDM+ fault recorder (legacy or current) | Substation | Medium
Hathaway DFR | DFR_DDR_001 |  | Hathaway (Qualitrol) digital fault recorder | Substation | High
Hathaway IDM | DFR_DDR_001; PMU_001 |  | Hathaway IDM fault and disturbance recorder with PMU option | Substation / grid | High
DDR | DFR_DDR_001 | MET_SAMPLING_RATE | Dynamic Disturbance Recorder (long-duration slow scan recording) | Substation / grid | High
dynamic disturbance recorder | DFR_DDR_001 |  | Long-duration slow scan recording of power system disturbances | Grid | High
CFR | DFR_DDR_001 |  | Continuous Fault Recorder (continuous DFR recording mode) | Substation | Medium
continuous fault recorder | DFR_DDR_001 |  | IDM+ continuous fault recording function | Substation | Medium
DFR | DFR_DDR_001 | MET_SAMPLING_RATE | Digital Fault Recorder | Substation / feeder | High
digital fault recorder | DFR_DDR_001 |  | Digital fault recording device | Substation | High
DFR panel | DFR_DDR_001; FMS_001 |  | Fault recording panel housing IDM+ and accessories | Substation panel | High
FRS panel | DFR_DDR_001; FMS_001 |  | Fault Recording System panel | Substation | High
FRS | DFR_DDR_001 |  | Fault Recording System (generic term for DFR system) | Substation | High
fault recording system | DFR_DDR_001 |  | Generic: fault recording system installed at substation | Substation | High
fault disturbance recorder | DFR_DDR_001 |  | Combined fault and disturbance recorder | Substation | High
disturbance monitor | DFR_DDR_001 |  | Power system disturbance monitoring | Substation / grid | Medium
IDM+ 9 | DFR_DDR_001 | MET_ANALOG_CHANNELS | IDM+ 9-channel variant (9A/32D, 3U) | Substation | High
IDM+ 18 | DFR_DDR_001 | MET_ANALOG_CHANNELS | IDM+ 18-channel variant (18A/64D, 6U) | Substation | High
IDM+ 36 | DFR_DDR_001 | MET_ANALOG_CHANNELS | IDM+ 36-channel variant (36A/128D, 6U) | Substation | High
IDM+ 9A | DFR_DDR_001 | MET_ANALOG_CHANNELS | IDM+ 9 analog channel configuration | Substation | High
IDM+ 18A | DFR_DDR_001 | MET_ANALOG_CHANNELS | IDM+ 18 analog channel configuration | Substation | High
IDM+ 36A | DFR_DDR_001 | MET_ANALOG_CHANNELS | IDM+ 36 analog channel configuration | Substation | High
SOE | DFR_DDR_001 |  | Sequence of Events recorder (function of IDM+) | Substation | Medium
sequence of events | DFR_DDR_001 |  | SOE recording of digital input state changes | Substation | Medium
waveform recorder | DFR_DDR_001 |  | Voltage/current waveform recording capability | Substation | Medium
WAMS | PMU_001; WAMS_001 | MET_REPORTING_RATE | Wide Area Monitoring System based on synchrophasors | Transmission grid | High
wide area monitoring | PMU_001; WAMS_001 |  | Wide-area phasor-based grid monitoring | Multi-site grid | High
wide area measurement | PMU_001; WAMS_001 |  | Wide Area Measurement System (IEEE C37.118) | Transmission grid | High
PDC | PMU_001; WAMS_001 |  | Phasor Data Concentrator (central collection point for PMU data) | Grid control center | High
phasor data concentrator | PMU_001; WAMS_001 |  | Central server for collecting and processing PMU data streams | Grid | High
IEEE C37.118 | PMU_001 | MET_REPORTING_RATE | IEEE standard for synchrophasor measurement | Grid / PMU | High
C37.118 | PMU_001 | MET_REPORTING_RATE | IEEE C37.118 PMU compliance standard | Grid / PMU | High
C37.118 2014 | PMU_001 |  | IEEE C37.118-2014 revised PMU standard | Grid / PMU | High
synchrophasor streaming | PMU_001 |  | Real-time phasor data streaming compliant with IEEE C37.118 | Grid | High
phasor measurement unit | PMU_001 | MET_REPORTING_RATE | Synchrophasor measurement device | Grid | High
PMU panel | PMU_001; FMS_001 |  | Panel housing PMU-enabled IDM+ devices | Substation | High
FMS | FMS_001; DFR_DDR_001 |  | Fault Monitoring System (iQ+ platform + DFR hardware at substation) | Multi-site grid | High
FL-8 | FAULT_LOC_001 | MET_LINE_COUNT | Qualitrol TWS FL-8 traveling wave fault locator (up to 8 lines) | Transmission line | High
FL-1 | FAULT_LOC_001 | MET_LINE_COUNT | Qualitrol TWS FL-1 single-line traveling wave fault locator | Transmission line | High
FL8 | FAULT_LOC_001 |  | TWS FL-8 fault locator abbreviation | Transmission line | High
FL1 | FAULT_LOC_001 |  | TWS FL-1 fault locator abbreviation | Transmission line | High
TWS FL-8 | FAULT_LOC_001 | MET_LINE_COUNT | Qualitrol TWS FL-8 product (modular, up to 8 lines) | Transmission line | High
TWS FL-1 | FAULT_LOC_001 |  | Qualitrol TWS FL-1 product (single-line, distributed substations) | Transmission line | High
linear coupler | FAULT_LOC_001 |  | CT secondary linear coupler for TWS traveling wave detection | Transmission line CT secondary | High
TWS card | FAULT_LOC_001 |  | TWS option card fitted in IDM+ for integrated fault location | Substation / IDM+ | High
FL2 | FAULT_LOC_001 | MET_LINE_COUNT | TWS FL-8 configured for 2-line monitoring (BOQ shorthand) | Transmission line | Medium
FL-2 | FAULT_LOC_001 | MET_LINE_COUNT | TWS FL-8 in 2-line configuration (site BOQ notation) | Transmission line | Medium
iQ+ | FMS_001; SUB_SOFT_001 |  | Qualitrol iQ+ Master Station software for DFR/TWS/PMU fleet management | Substation server | High
iQ plus | FMS_001; SUB_SOFT_001 |  | iQ+ Master Station (alternate spelling) | Substation server | High
master station | FMS_001; SUB_SOFT_001 |  | iQ+ centralized master station software | Substation server | High
iQ master station | FMS_001; SUB_SOFT_001 |  | Qualitrol iQ+ Master Station application | Substation server | High
CASHEL FMS | FMS_001 |  | CASHEL (Qualitrol brand name for FMS panels/server system) | Substation FMS | High
CASHEL server | FMS_001 |  | Rackmount server included in CASHEL FMS system | Substation server | High
FMS server | FMS_001 |  | Fault Management System server (iQ+ host) | Substation server | High
GridAssist | FMS_001; SUB_SOFT_001 |  | Qualitrol GridAssist substation monitoring platform | Substation / fleet | Medium
central server | FMS_001 |  | Central iQ+ server for multi-DFR data collection | Substation server | Medium
substation data server | FMS_001 |  | Server infrastructure for substation monitoring data management | Substation server | Medium
SmartSub | SUB_SOFT_001 |  | Qualitrol SmartSub substation asset performance management platform | Substation / fleet | High
PDMG-RH | GIS_PD_001 | MET_SENSOR_TYPE | Qualitrol PDMG-RH GIS PD monitoring system (Gen 3) | GIS | High
PDMG | GIS_PD_001 | MET_SENSOR_TYPE | PDMG series partial discharge monitor for GIS | GIS | High
GIS PDM | GIS_PD_001 |  | GIS Partial Discharge Monitor (generic abbreviation) | GIS | High
UHF coupler | GIS_PD_001 | MET_SENSOR_TYPE | UHF sensor/coupler installed on GIS for PD detection | GIS | High
OCU | GIS_PD_001 |  | Optical Converter Unit (signal conditioner in PDMG-RH system) | GIS PDM system | Medium
optical converter unit | GIS_PD_001 |  | OCU signal conditioning unit in PDMG-RH GIS PD system | GIS | Medium
arc detection | GIS_ARC_001; GIS_PD_001 |  | GIS arc flash/discharge detection capability (PDMG-RH Gen3 feature) | GIS | High
arc flash | GIS_ARC_001 |  | Arc flash event in GIS requiring detection and localization | GIS | High
flashover | GIS_ARC_001 |  | GIS internal flashover event (arc discharge) | GIS | High
GIS flashover | GIS_ARC_001 |  | Flashover in gas-insulated switchgear compartment | GIS | High
arc localization | GIS_ARC_001 |  | Pinpointing arc location in GIS compartment to enable fast bay re-energization | GIS | High
QBCM | BRK_HEALTH_001 |  | Qualitrol QBCM circuit breaker condition monitor | Circuit breaker | High
BCM | BRK_HEALTH_001 |  | Circuit breaker condition monitor (generic / Qualitrol product) | Circuit breaker | High
breaker condition monitor | BRK_HEALTH_001 |  | Online condition monitor for high-voltage circuit breakers | HV circuit breaker | High
CBT 200 | BRK_HEALTH_001 |  | Hathaway CBT 200 circuit breaker monitor | Circuit breaker | Medium
BCM 200 | BRK_HEALTH_001 |  | Hathaway BCM 200/200E circuit breaker monitor | Circuit breaker | Medium
INFORMA PMD-A | PQ_CLASSA_001 | MET_PQ_CLASS | Qualitrol INFORMA PMD-A Class A power quality monitor | PCC / bus / feeder | High
PMD-A | PQ_CLASSA_001 | MET_PQ_CLASS | INFORMA PMD-A power quality monitor (abbreviated) | PCC / feeder | High
INFORMA | PQ_CLASSA_001 |  | Qualitrol INFORMA series power quality monitors | PCC / bus | Medium
power system monitor | DFR_DDR_001; PQ_CLASSA_001 |  | Multifunction substation monitor (IDM+ / INFORMA PMD-A) | Substation | Medium
TM1 | TR_DGA_001 | MET_DGA_GAS_COUNT | Qualitrol Serveron TM1 single-gas DGA monitor | Transformer | High
TM3 | TR_DGA_001 | MET_DGA_GAS_COUNT | Qualitrol Serveron TM3 3-gas DGA monitor | Transformer | High
TM8 | TR_DGA_001 | MET_DGA_GAS_COUNT | Qualitrol Serveron TM8 8-gas DGA monitor | Transformer | High
Serveron | TR_DGA_001 |  | Qualitrol Serveron online DGA monitor series | Transformer | High
inter-area oscillation | WAMS_001; PMU_001 |  | Low-frequency power swing between grid areas (WAMS use case) | Transmission grid | High
power swing monitoring | WAMS_001; PMU_001 |  | Wide-area monitoring of power system oscillations | Transmission grid | High
frequency disturbance | WAMS_001; DFR_DDR_001 |  | System frequency deviation event (DFR or WAMS scope) | Grid | Medium

## 06_Product_Family_Master
Product Family Master - Product Families Before Actual Models
Use this as the first-level product candidate table. Actual product models should be added in the Product Master Template.
Product Family ID | Product Family | Applicable Scenario IDs | Primary Asset Type | Typical Capabilities | Default Quantity Rule ID | Dependencies / Required Inputs | Commercial / Engineering Notes
| Family display name; shown in outputs & research. | ';'-separated scenario IDs (sheet 03) this family serves; drives matching. | Main asset type (research prompt context). | ';'-separated capabilities; used in product research. | Quantity rule (sheet 09) used when researching this family. | Inputs needed; used as research context. | Human note; not used by the pipeline.
PF_DGA | Online DGA Monitor | TR_DGA_001 | Oil-filled transformer | Online dissolved gas monitoring; moisture; oil temperature; alarm outputs; SCADA integration | QR_TR_DGA_001 | Transformer count; oil type; gas count requirement; protocol; power supply | Actual product models and gas capabilities must be validated by product team.
PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Oil/winding temperature monitoring; fan/cooling control; alarm/trip contacts | QR_TR_TEMP_001 | Transformer count; temperature points; fan stages; alarm contacts | Differentiate oil-filled and dry-type transformer applications.
PF_BUSHING | Bushing Monitor | TR_BUSH_001 | Transformer bushing | Capacitance/tan delta/leakage current monitoring; phase comparison; alarms | QR_TR_BUSH_001 | Transformer count; bushing count; voltage level; phase configuration | Channel count must be confirmed.
PF_PD_TRANSFORMER | Transformer PD Monitor | TR_PD_001 | Power transformer | Partial discharge monitoring with selected sensor methods; alarm and trend monitoring | QR_TR_PD_001 | Transformer design; sensor type; monitoring zones; voltage level | Sensor placement requires engineering review.
PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Pressure relief; oil level; oil flow; Buchholz relay; contact outputs; environmental sensing | QR_TR_AUX_001 | Accessory list; mounting; contact type; alarm/trip logic | Often OEM or retrofit accessory scope.
PF_BREAKER | Circuit Breaker Monitor | BRK_HEALTH_001 | Circuit breaker | Trip/close timing; coil current; operation count; mechanism health; optional SF6 signals | QR_BRK_001 | Breaker count; breaker type; coil voltage; auxiliary contacts; SF6 requirement | One monitor per breaker is a default assumption only.
PF_GIS_PD | GIS PD Monitor | GIS_PD_001 | GIS bay | UHF partial discharge monitoring; bay/compartment monitoring; alarm/trend software | QR_GIS_PD_001 | GIS layout; bay count; compartments; voltage level; sensor placement | Do not finalize quantity without GIS layout.
PF_SWG_PD | MV Switchgear PD Monitor | SWG_PD_001 | MV switchgear | TEV/HFCT/UHF sensor options; feeder/panel PD monitoring; trend and alarms | QR_SWG_PD_001 | Panel count; feeder count; sensor type; voltage level | Scope may be panel-level or feeder-level.
PF_GEN_PD | Generator PD Monitor | GEN_PD_001 | Generator | Online/offline stator partial discharge monitoring; couplers/sensors; trends and alarms | QR_GEN_PD_001 | Generator count; voltage; rating; coupler count; online/offline mode | Iris Power-related product expertise required.
PF_GEN_EWV | Generator End-Winding Vibration Monitor | GEN_EWV_001 | Generator | End-winding vibration sensors; trend monitoring; alarms | QR_GEN_EWV_001 | Generator count; sensor locations; speed; vibration thresholds | Engineering review required.
PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Air gap monitoring; rotor flux; eccentricity; unit-level monitoring | QR_GEN_AIRGAP_001 | Hydro unit count; pole count; sensor layout; speed | Strongly drawing/design dependent.
PF_MOTOR | Motor Monitor | MTR_PD_001; MTR_TEMP_001 | Large motor | Motor PD; temperature; RTD/bearing temperature; condition monitoring | QR_MOTOR_001 | Motor list; voltage/rating; RTD count; criticality; sensor count | Prioritize critical large motors.
PF_PQ | Power Quality Recorder | PQ_CLASSA_001; RENEWABLE_PCC; DATA_CENTER_POWER | PCC / bus / feeder | Class A PQ; harmonics; flicker; sag/swell; transient event recording | QR_PQ_001 | PCC count; voltage/current channels; PQ class; standard; time sync | Class A requirement must be treated as must-have.
PF_DFR | Digital Fault / Disturbance Recorder | DFR_DDR_001; FAULT_LOC_001 | Substation / feeder / plant bus | Waveform/event recording; trigger logic; time synchronization; channel recording | QR_DFR_001 | Channel list; voltage/current inputs; sampling rate; trigger; time sync | Channel count drives configuration and quantity.
PF_PMU | Phasor Measurement Unit | PMU_001 | Grid measurement point | Synchrophasor measurement; reporting rate; time sync; grid monitoring | QR_PMU_001 | Measurement points; reporting rate; standard; time sync; channel count | May be standalone or integrated with recorder.
PF_SOFTWARE | Monitoring Software / Asset Platform | SUB_SOFT_001; COMM_SCADA_001 | Multi-asset / site / fleet | Dashboards; alarms; historian/SCADA integration; analytics; fleet view | QR_SOFT_001 | Site count; asset count; data points; protocol; license model | License model and commercial rules must be confirmed.
PF_GATEWAY | Communication Gateway / Integration Module | COMM_SCADA_001 | Monitoring system | Protocol conversion; SCADA interface; network connectivity; cybersecurity support | QR_GATEWAY_001 | Protocol; network topology; device count; cybersecurity constraints | May be accessory or stand-alone integration line.
PF_TWS | Traveling Wave Fault Locator | FAULT_LOC_001 | Transmission line / feeder | Traveling wave detection; single-end and double-end fault location; GPS/IEEE 1588 time sync; line protection relay integration; sub-cycle fault location accuracy | QR_FAULT_LOC_001 | Line count; line length (km); wave propagation velocity; GPS time-sync availability; CT/VT channel count; relay integration requirement | Qualitrol TWS FL-2 product confirmed in reference quotes. Confirm whether integrated with DFR or standalone. Verify channel count and line configuration.
PF_DAU_REC | Multi-function DAU / Recorder (IDM+ / Informa) | FMS_001;DFR_DDR_001;PMU_001;WAMS_001;PQ_CLASSA_001 | Bay / Feeder | Combined fault/disturbance (FMS/DFR), power-quality (PQM) and phasor (PMU/WAMS) recording delivered on one DAU family; installed per monitored bay; channel variants 9A/32D, 18A/32D, 27A/64D. | QR_DAU_BAY_001 | Monitored bay count per voltage level & function | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PF_MON_PANEL | Monitoring Panel / Cabinet | FMS_001;PMU_001;WAMS_001;PQ_CLASSA_001 | Panel | FMS/PQM/WAMS field panels and LEV/PDC system cabinets housing the DAUs, industrial PC, network and GPS equipment. | QR_PANEL_001 | DAU count; panels per Transco spec | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PF_NET_SEC | Network & Security Equipment | COMM_SCADA_001 | Panel | Managed L2/L3 Ethernet switches (RJ45 + fiber) and firewalls for the monitoring LAN and integration to LDC/TCC. | QR_PER_PANEL_001 | Panel count; comms architecture | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PF_TIMING | GPS Timing | PMU_001;WAMS_001 | System | GPS antenna + cable + amplifier + surge arrestor and GPS splitters for time-synchronised PMU/WAMS recording. | QR_PER_SYSTEM_001 | Time-sync requirement (PMU/WAMS present) | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PF_SW_LIC | Monitoring Software & Licences | COMM_SCADA_001;PMU_001;WAMS_001 | System | iQ+ master-station software, EPG PMU/WAMS licences, and cyber software (antivirus / whitelisting / backup) — normally one set per substation. | QR_PER_SYSTEM_001 | User/device tiers; licence counts | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PF_SERVICES | Engineering & Commissioning Services | COMM_SCADA_001 | System | Factory FAT, testing & commissioning, communication establishment, cybersecurity, energisation assistance, training and spares (day-rate). | QR_SERVICES_001 | Scope size drives service days | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PF_PANEL_ACC | Panel Accessories | FMS_001;PMU_001;PQ_CLASSA_001 | Bay | Per-DAU / per-panel wiring accessories such as test switches. | QR_PER_DAU_001 | DAU count | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.

## 07_Product_Master_Template
Product Master Template - Fill Actual Qualitrol Product Models
Actual product models, supported standards, protocols, and datasheet URLs are intentionally left blank where not available.
Product ID | Product Model | Product Family ID | Product Family | Applicable Scenario IDs | Primary Asset Type | Product Description | Supported Standards | Communication Protocols | Default Quantity Rule ID | Required Accessories | Optional Accessories | Datasheet URL | Source Owner | Status | Notes
| Actual model; presence means capability is known in matching. | Links product to its family (sheet 06). | Family display name. | Reference; matching uses family-level scenarios, not this. | Reference; family-level asset type is used instead. | Reference/display; not used in matching. | Reference/display; not used in matching. | Reference/display; not used in matching. | Reference; quantity uses the scenario rule (sheet 09). | Reference only; NOT read by the pipeline. | Reference only; NOT read by the pipeline. | Source link; written by maintenance scripts, not read by matching. | Provenance; written by maintenance scripts, not read by matching. | Candidate/Verified/TBD; TBD with no model blocks a firm match. | Human note; not used by matching.
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | Online DGA Monitor | TR_DGA_001 | Oil-filled transformer | On-line single-gas (hydrogen) DGA monitor with solid-state sensor immersed directly in oil; monitors hydrogen, oil temperature and moisture-in-oil for power transformers. | IEC 61010-1; IEC 61010-2-81; UL 61010-1; CSA-C22.2 No. 61010-1-04; EN 61326-1; CISPR 11; IEC 61000 series; IEC 60255-21-1 | DNP3, Modbus | QR_TR_DGA_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM1_ad935707.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\TM1_ad935707.pdf'; verify before quoting.
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | Online DGA Monitor | TR_DGA_001 | Oil-filled transformer | On-line DGA monitor using laboratory grade Gas Chromatography, correlating 3 fault gases (acetylene, ethylene, methane), moisture-in-oil, oil temperature and ambient temperature to transformer load. | IEEE, IEC 60599-2007-05, ASTM, CIGRE, IEC 61010-1, UL 61010-1, CSA-C22.2 No.61010-1-04, EN 61326-1 | TCP/IP, DNP3, Modbus RTU, ASCII, OPC, IEC 61850 | QR_TR_DGA_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\TM3_73e234b6.pdf'; verify before quoting.
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | Online DGA Monitor | TR_DGA_001 | Oil-filled transformer | On-line DGA monitor measuring 8 fault gases plus nitrogen, moisture and oil temperature using laboratory grade gas chromatography. | IEEE C57.104-2008, IEC 60599-2007-05, ASTM, CIGRE, EN 61010-1, UL 61010-1, EN 61326-1:2006 | TCP/IP, DNP3, Modbus RTU, ASCII, OPC, IEC 61850 | QR_TR_DGA_001 |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Software_Solutions\TMView_8bc233a4.pdf'; verify before quoting.
PROD_PF_PD_TRANSFORMER_01 | QPDM | PF_PD_TRANSFORMER | Transformer PD Monitor | TR_PD_001 | Power transformer | Continuous online UHF Partial Discharge monitor for transformers with real-time PD amplitude and discharge rate monitoring, trending, and fault classification. IP66 rated enclosure with built-in LED indicators and remote client. | CIGRE life management guidelines |  | QR_TR_PD_001 |  |  | https://www.qualitrolcorp.com/products/QPDM |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PD_TRANSFORMER_02 | QPPDM | PF_PD_TRANSFORMER | Transformer PD Monitor | TR_PD_001 | Power transformer | Portable partial discharge monitor for transformers and GIS. |  |  | QR_TR_PD_001 |  |  | https://www.qualitrolcorp.com/products/QPPDM |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_BREAKER_01 | QBCM | PF_BREAKER | Circuit Breaker Monitor | BRK_HEALTH_001 | Circuit breaker | Advanced Circuit Breaker Monitoring System with intelligent analytics for monitoring breaker health including SF6 density trends, travel curves, coil current signatures, electrical wear calculations, and operating mechanism performance. | IEC 61850, COMTRADE | IEC 61850, COMTRADE | QR_BRK_001 |  |  | https://www.qualitrolcorp.com/products/QBCM |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_BREAKER_02 | QBCM Software | PF_BREAKER | Circuit Breaker Monitor | BRK_HEALTH_001 | Circuit breaker | Circuit Breaker Monitoring & Diagnostics Software for automated data processing, trend analysis, and predictive maintenance scheduling. | IEC 61850, COMTRADE | IEC 61850, COMTRADE | QR_BRK_001 |  |  | https://www.qualitrolcorp.com/products/QBCM-Software |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_BREAKER_03 | HATHAWAY CBT 200/400 | PF_BREAKER | Circuit Breaker Monitor | BRK_HEALTH_001 | Circuit breaker | Hathaway Breaker Condition Monitor listed in Qualitrol Product Overview Catalog under Breaker Condition Monitors. |  |  | QR_BRK_001 |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_BREAKER_04 | HATHAWAY BCM 200/200E | PF_BREAKER | Circuit Breaker Monitor | BRK_HEALTH_001 | Circuit breaker | Hathaway Breaker Condition Monitor listed in Qualitrol Product Overview Catalog under Breaker Condition Monitors. |  |  | QR_BRK_001 |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GIS_PD_01 | Gen 3 PDM | PF_GIS_PD | GIS PD Monitor | GIS_PD_001 | GIS bay | Online PD monitoring and Arc Monitor for GIS using UHF sensors with IEC 61850 support. | IEC 61850 | IEC 61850 | QR_GIS_PD_001 |  |  | https://www.qualitrolcorp.com/products/Gen3PDM |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GIS_PD_02 | PDMG-RH - Gen 3 | PF_GIS_PD | GIS PD Monitor | GIS_PD_001 | GIS bay | Qualitrol DMS PDMG-RH GIS Partial Discharge Monitor for UHF partial discharge monitoring of gas-insulated switchgear. |  |  | QR_GIS_PD_001 |  |  | https://www.qualitrolcorp.com/products/PDMG |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GIS_PD_03 | Portable PDM | PF_GIS_PD | GIS PD Monitor | GIS_PD_001 | GIS bay | Portable partial discharge monitor for transformers and GIS using UHF technology; hand-carry system with touch interface and intelligent data handling (SMARTSUB Software). |  | Ethernet (RJ45 10/100 Mbps), USB | QR_GIS_PD_001 |  |  | https://smsystems.co.in/qualitrol/pdf/PD-D27-10L-01E_Portable_PDM.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GIS_PD_04 | QPDM | PF_GIS_PD | GIS PD Monitor | GIS_PD_001 | GIS bay | Next generation UHF continuous online partial discharge monitor for transformers (related to GIS PD monitoring family); high dynamic range, real-time amplitude and discharge rate trending, IP66 enclosure. |  |  | QR_GIS_PD_001 |  |  | https://www.qualitrolcorp.com/products/QPDM |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MV Switchgear PD Monitor | SWG_PD_001 | MV switchgear | Continuous online UHF partial discharge monitor for transformers; real-time PD amplitude and discharge rate monitoring, trending and classification. | IEC 60270; CIGRE life management guidelines | Ethernet (RJ45/fiber); IEC 61850; Modbus | QR_SWG_PD_001 |  |  | https://www.qualitrolcorp.com/products/QPDM |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_SWG_PD_02 | QPPDM | PF_SWG_PD | MV Switchgear PD Monitor | SWG_PD_001 | MV switchgear | Qualitrol portable partial discharge monitor for transformer and GIS PD measurement. |  |  | QR_SWG_PD_001 |  |  | https://www.qualitrolcorp.com/products/QPPDM |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_SWG_PD_03 | PDMG-RH Gen 3 | PF_SWG_PD | MV Switchgear PD Monitor | SWG_PD_001 | MV switchgear | DMS PDMG-RH GIS partial discharge monitor (Generation 3) for gas insulated switchgear. |  |  | QR_SWG_PD_001 |  |  | https://www.qualitrolcorp.com/products/PDMG |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_SWG_PD_04 | IC44 | PF_SWG_PD | MV Switchgear PD Monitor | SWG_PD_001 | MV switchgear | Qualitrol IC44 UHF partial discharge coupler sensor for PD detection. |  |  | QR_SWG_PD_001 |  |  | https://www.qualitrolcorp.com/products/IC44 |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GEN_PD_01 | PDTracII 4208 | PF_GEN_PD | Generator PD Monitor | GEN_PD_001 | Generator | Continuous partial discharge measurement system for motors/generators using Iris Power Epoxy Mica Capacitor Couplers. |  |  | QR_GEN_PD_001 |  |  | https://www.qualitrolcorp.com/products/PDTracII |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GEN_PD_02 | TGA-S | PF_GEN_PD | Generator PD Monitor | GEN_PD_001 | Generator | Portable periodic on-line partial discharge monitoring instrument for motors and turbine generators using SSC sensors | IEEE Std. 1434-2014; IEEE Std.1129; IEC 60034-27-2:2012 | USB; Ethernet | QR_GEN_PD_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-S_c922447e.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\TGA-S_c922447e.pdf'; verify before quoting.
PROD_PF_GEN_EWV_01 | EVAII | PF_GEN_EWV | Generator End-Winding Vibration Monitor | GEN_EWV_001 | Generator | Iris Power EVAII fiber optic accelerometer vibration sensor kit for endwinding vibration monitoring on air-cooled machines. |  |  | QR_GEN_EWV_001 |  |  | https://www.qualitrolcorp.com/products/EVAII |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GEN_EWV_02 | GuardII+ | PF_GEN_PD | Generator PD Monitor | GEN_PD_001 | Generator | Continuous online monitor for stator and rotor windings of large generators and high voltage motors; combines multiple condition monitoring technologies (PD, rotor magnetic flux, endwinding vibration, shaft current/voltage) in one box. |  | Modbus; USB; RJ45; fiber optic (optional) | QR_GEN_PD_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/GuardII+_fcc4ac4b.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\GuardII+_fcc4ac4b.pdf'; verify before quoting.
PROD_PF_GEN_EWV_03 | EVTracII | PF_GEN_EWV | Generator End-Winding Vibration Monitor | GEN_EWV_001 | Generator | Iris Power EVTracII online instrument for continuous end winding vibration monitoring. |  |  | QR_GEN_EWV_001 |  |  | https://offers.qualitrolcorp.com/direct-current |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GEN_AIRGAP_01 | Iris Power TFProbe | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Magnetic flux probe designed for hydrogenerators and salient pole machines with air gap size less than 50mm to detect shorted rotor winding turns. |  |  | QR_GEN_AIRGAP_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/FFProbe_-_Rotor_Flux_Monitoring_86c050b4.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\FFProbe_-_Rotor_Flux_Monitoring_86c050b4.pdf'; verify before quoting.
PROD_PF_GEN_AIRGAP_02 | Iris Power FFProbe | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Magnetic flux probe used in turbine generators with air gap size 50mm and over to detect shorted rotor winding turns; foldable layout for rotor introduction. |  |  | QR_GEN_AIRGAP_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/FFProbe_-_Rotor_Flux_Monitoring_86c050b4.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\FFProbe_-_Rotor_Flux_Monitoring_86c050b4.pdf'; verify before quoting.
PROD_PF_GEN_AIRGAP_03 | Iris Power Capacitive Air Gap Sensor (CGS) | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Capacitive air gap sensor for continuous on-line air gap monitoring of hydro generators. Measures distance between rotor and stator; output directly proportional to air gap distance (pole profile). Kit includes probes, linearization modules, junction box and installation materials. | None | None | QR_GEN_AIRGAP_001 |  |  | https://irispower.com/wp-content/uploads/2016/11/Iris-Power-CGS-Brochure-Capacitive-Gap-Sensor-1.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GEN_AIRGAP_04 | Iris Power TGA-S | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Iris Power TGA monitor for generator stator winding partial discharge monitoring. | None | None | QR_GEN_AIRGAP_001 |  |  | https://www.qualitrolcorp.com/products/TGA-S |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GEN_AIRGAP_05 | Iris Power GuardII+ | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Iris Power GuardII+ continuous on-line partial discharge monitor for generators. | None | None | QR_GEN_AIRGAP_001 |  |  | https://www.qualitrolcorp.com/products/GuardIIPlus |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_MOTOR_01 | PDTracII 4208 | PF_MOTOR | Motor Monitor | MTR_PD_001; MTR_TEMP_001 | Large motor | System providing continuous partial discharge measurement in motors using Iris Power Epoxy Mica Capacitor Couplers | None | None | QR_MOTOR_001 |  |  | https://www.qualitrolcorp.com/products/PDTracII |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_MOTOR_02 | PPM-97 Corona Probe | PF_MOTOR | Motor Monitor | MTR_PD_001; MTR_TEMP_001 | Large motor | Offline partial discharge locator (corona probe) for motors and generators | None | None | QR_MOTOR_001 |  |  | https://www.qualitrolcorp.com/products/PPM-97 |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_MOTOR_03 | PPM-97 TGA-B | PF_MOTOR | Motor Monitor | MTR_PD_001; MTR_TEMP_001 | Large motor | Iris Power TGA monitor | None | None | QR_MOTOR_001 |  |  | https://www.qualitrolcorp.com/products/TGA-B |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PQ_01 | BEN 6000 | PF_PQ | Power Quality Recorder | PQ_CLASSA_001; RENEWABLE_PCC; DATA_CENTER_POWER | PCC / bus / feeder | Extreme digital fault recorder with optional Class A power quality monitoring; flexible upgradeable device usable as DFR, DSM, DDR, continuous recorder, Class A PQ meter, PMU, fault locator and SOE. Up to 192 analog channels and 384 digital channels in central or distributed architecture; up to 4 PQ cards in parallel. | IEC 61000-4-30 Class A; IEC 61000-3-6/7; IEC 61850; IEEE C37.111 COMTRADE; NERC compliant | IEC 61850 GOOSE | QR_PQ_001 |  |  | https://www.leane.it/sites/default/files/prodotti/BEN_6000.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PQ_02 | BEN 6000 PORTABLE | PF_PQ | Power Quality Recorder | PQ_CLASSA_001; RENEWABLE_PCC; DATA_CENTER_POWER | PCC / bus / feeder | Portable extreme digital fault recorder for temporary/quick disturbance system monitoring, power generation dynamic monitoring, fault recording, synchrophasor measurement, SOE and/or Class A power quality monitoring. 16 analog and 16 digital channels, expandable via remote acquisition units. | IEC 61000-4-30 Class A; IEC 61850 | IEC 61850 GOOSE | QR_PQ_001 |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PQ_03 | BEN 600 | PF_PQ | Power Quality Recorder | PQ_CLASSA_001; RENEWABLE_PCC; DATA_CENTER_POWER | PCC / bus / feeder | Extreme digital fault recorder for digital fault recording and power generation monitoring with multifunctional capabilities including disturbance system monitoring, synchrophasor measurement, SOE and/or Class A power quality monitoring. | IEC 61000-4-30 Class A; IEC 61850 | IEC 61850 GOOSE | QR_PQ_001 |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PQ_04 | IDM | PF_PQ | Power Quality Recorder | PQ_CLASSA_001; RENEWABLE_PCC; DATA_CENTER_POWER | PCC / bus / feeder | Hathaway IDM digital fault recorder for fault recording and dynamic monitoring; usable as DFR, disturbance system monitor, continuous fault recorder, synchrophasor measurement unit, impedance based fault locator and power quality monitoring. | Class A power quality (optional) | IEC 61850 GOOSE (optional) | QR_PQ_001 |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PQ_05 | IDM+ | PF_PQ | Power Quality Recorder | PQ_CLASSA_001; RENEWABLE_PCC; DATA_CENTER_POWER | PCC / bus / feeder | IDM+ multi-function power system monitor. |  |  | QR_PQ_001 |  |  | https://www.qualitrolcorp.com/products/IDMPlus |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PMU_01 | HATHAWAY IDM | PF_PMU | Phasor Measurement Unit | PMU_001 | Grid measurement point | Digital fault recorder with synchrophasor measurement unit capability, used as digital fault recorder, disturbance system monitor, continuous fault recorder, PMU, impedance based fault locator and power quality monitor. | IEEE C37.118; IEC 61850 | IEC 61850 Goose messaging | QR_PMU_001 |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PMU_02 | HATHAWAY IDM PORTABLE | PF_PMU | Phasor Measurement Unit | PMU_001 | Grid measurement point | Portable digital fault recorder for mobile digital fault recording and dynamic monitoring, supporting synchrophasor measurement, impedance based fault location and power quality monitoring. | IEEE C37.118; IEC 61850 | IEC 61850 Goose messaging | QR_PMU_001 |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_PMU_03 | BEN 6000 PORTABLE | PF_PMU | Phasor Measurement Unit | PMU_001 | Grid measurement point | Portable extreme digital fault recorder for mobile fault recording and power generation monitoring, supporting synchrophasor measurement, sequence of events recording and Class A power quality monitoring. | IEEE C37.118; IEC 61850 | IEC 61850 Goose messaging | QR_PMU_001 |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_SOFTWARE_01 | ITM Remote | PF_SOFTWARE | Monitoring Software / Asset Platform | SUB_SOFT_001; COMM_SCADA_001 | Multi-asset / site / fleet | Advanced transformer life management software integrated with 509 ITM Intelligent Transformer Monitors, featuring proprietary TransLife technology for thermal modeling, life consumption analysis, and multi-winding monitoring. |  |  | QR_SOFT_001 |  |  | https://www.qualitrolcorp.com/knowledge-center/blogs/qualitrol-blog/asset-management-software |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_SOFTWARE_02 | SmartSub | PF_SOFTWARE | Monitoring Software / Asset Platform | SUB_SOFT_001; COMM_SCADA_001 | Multi-asset / site / fleet | Modular, scalable substation asset performance management platform integrating with existing infrastructure to provide comprehensive asset visibility through advanced sensor networks and intelligent analytics. |  |  | QR_SOFT_001 |  |  | https://www.qualitrolcorp.com/products/SmartSUB |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_SOFTWARE_03 | iQ+ Master Station | PF_SOFTWARE | Monitoring Software / Asset Platform | SUB_SOFT_001; COMM_SCADA_001 | Multi-asset / site / fleet | Software package for configuration, collection and analysis of data from Qualitrol Information Products with scalable client-server architecture and Record Analysis diagnostics. | EN 50160; IEC 61000-3-6; IEC 61000-3-7 | TCP/IP; COMTRADE; PQDIF | QR_SOFT_001 |  |  | Preparation/Qualitrol Product/Software_Solutions/IQ+_68057b47.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Software_Solutions\IQ+_68057b47.pdf'; verify before quoting.
PROD_PF_SOFTWARE_04 | TMView | PF_SOFTWARE | Monitoring Software / Asset Platform | SUB_SOFT_001; COMM_SCADA_001 | Multi-asset / site / fleet | Qualitrol/Serveron transformer monitoring software dashboard. |  |  | QR_SOFT_001 |  |  | https://www.qualitrolcorp.com/products/TMView |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_SOFTWARE_05 | QTMS | PF_SOFTWARE | Monitoring Software / Asset Platform | SUB_SOFT_001; COMM_SCADA_001 | Multi-asset / site / fleet | Transformer Monitoring System with modular design and web-based software for condition based, continuous online monitoring of transformer health. Supports hot-swappable, field-upgradeable modules and interfaces with Qualitrol and third-party smart sensors. | IEC 61850; IEC 60870-104-5; DNP 3.0 (Level 3); Modbus | Serial: DNP 3.0 (Level3), Modbus, IEC 60870-104-5; Ethernet: IEC 61850, IEC 60870-104-5, DNP 3.0 (Level 3), Modbus | QR_SOFT_001 |  |  | https://vainstein-ingenieros.com/wp-content/uploads/2024/01/QTMS.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_GATEWAY_01 | QGateway (GTW-SP-EP) | PF_GATEWAY | Communication Gateway / Integration Module | COMM_SCADA_001 | Monitoring system | Qualitrol compact and rugged IEC 61850 gateway providing direct serial link to IEC 61850 Smart Grid protocol; links up to two serial devices simultaneously and extends distance between control cabinets and control room using TCP/IP. Also supports Modbus, DNP 3.0 and IEC 60870-5-104. | IEC 61850; IEC 60870-5-104; IEC 61000-4-2/3/4/5/6/8; IEC 60255-5; IEEE C37.90; IEEE C37.90.1-2002; ISO 9001 | Modbus, DNP 3.0, IEC 61850, IEC 60870-5-104, HTTP (web server) | QR_GATEWAY_001 |  |  | http://www.neoptix.com/literature/ap-m09-21l-01a_qgateway_120509.pdf |  | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_DFR_01 | IDM+ | PF_DFR | Digital Fault / Disturbance Recorder | DFR_DDR_001; FAULT_LOC_001 | Substation / feeder / plant bus | Multifunction substation power system monitor combining DFR, DDR, PMU, TWS fault location and Class A PQ in one device. Three variants: IDM+ 9, IDM+ 18, IDM+ 36. | IEEE C37.118-2005; IEC 61000-4-30 Class A (Ed 2.0); IEC 61000-4-7; IEC 61000-4-15; COMTRADE; NERC cyber security | IEC 61850; IEC 60870-5; DNP; Modbus; NTP; ethernet (RJ45/fibre); modem; serial | QR_DFR_001 |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'The_Power_Grid\IDM+_22da82f9.pdf'; verify before quoting.
PROD_PF_DFR_02 | iQ+ | PF_DFR | Digital Fault / Disturbance Recorder | DFR_DDR_001; FAULT_LOC_001 | Substation / feeder / plant bus | iQ+ Master Station Software for managing fault/disturbance recording data across the power grid. | None | None | QR_DFR_001 |  |  | https://www.qualitrolcorp.com/products/IQPlus | Tavily research (pending review) | Verified | Sourced via Tavily web research; verify before quoting.
PROD_PF_TWS_01 | HATHAWAY MARK VI | PF_TWS | Traveling Wave Fault Locator | FAULT_LOC_001 | High voltage transmission line | Traveling wave fault locator for single-end or double-end fault location on high-voltage transmission lines. Supports up to 8 monitored lines per device with DNP 3.0 SCADA interface. |  | DNP 3.0 |  |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf | Tavily research (pending review) | Verified | Sourced via Tavily; verify model name and availability.
PROD_PF_TWS_02 | HATHAWAY DSFL | PF_TWS | Traveling Wave Fault Locator | FAULT_LOC_001 | High voltage transmission line | Digital Single-ended Fault Locator; traveling wave based; suitable for single-end fault location without GPS synchronization requirement at remote end. | [5 empty] | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf | Tavily research (pending review) | Verified | Sourced via Tavily; verify model name and availability.
PROD_PF_TWS_03 | IDM+ (TWS function) | PF_TWS | Traveling Wave Fault Locator | FAULT_LOC_001; DFR_DDR_001; PMU_001 | Transmission line | IDM+ multi-function recorder with integrated traveling wave fault location capability, GPS time reference with 100 ns precision time tagging. | [5 empty] | https://www.qualitrolcorp.com/knowledge-center/blogs/qualitrol-blog/traveling-wave-fault-location | Tavily research (pending review) | Verified | Sourced via Tavily; IDM+ covers DFR+PMU+TWS in one device. Verify licensing.
PROD_PF_DFR_03 | IDM+ 9 | PF_DFR | Digital Fault / Disturbance Recorder | DFR_DDR_001; PMU_001; FAULT_LOC_001; PQ_CLASSA_001 | Substation / feeder / plant bus | IDM+ 9: 9 analog and 32 digital channels (3U, 19-inch rack). Smallest IDM+ variant. Functions: DFR (512 samples/cycle), DDR, optional PMU (IEEE C37.118 2014), optional TWS card (±60m FL), optional Class A PQ (IEC 61000-4-30 Class A Ed.2). | IEEE C37.118-2014; IEC 61000-4-30 Class A; IEC 61850 | IEC 61850; IEC 60870-5-104; DNP 3.0; Modbus | QR_DFR_001 |  | GPS antenna; IRIG-B module; GPS splitter | https://www.qualitrolcorp.com/products/IDMPlus | Verified via Tavily web research + Gemba Samples BOQ/product manuals. | Verified | BOQ shorthand: IDM+ 9A/32D. 3U rackmount. Weight 15 kg. Sampling: 30.7 kHz@60Hz / 25.6 kHz@50Hz. Storage: 4 GB (opt. 16 GB). GPS time tagging: 100 ns.
PROD_PF_DFR_04 | IDM+ 18 | PF_DFR | Digital Fault / Disturbance Recorder | DFR_DDR_001; PMU_001; FAULT_LOC_001; PQ_CLASSA_001 | Substation / feeder / plant bus | IDM+ 18: 18 analog and 64 digital channels (6U, 19-inch rack). Mid-range IDM+ variant for substations with more feeders. Same optional functions as IDM+ 9 (PMU, TWS, Class A PQ). | IEEE C37.118-2014; IEC 61000-4-30 Class A; IEC 61850 | IEC 61850; IEC 60870-5-104; DNP 3.0; Modbus | QR_DFR_001 |  | GPS antenna; IRIG-B; TWS card (optional) | https://www.qualitrolcorp.com/products/IDMPlus | Verified via Tavily web research + Gemba Samples BOQ/product manuals. | Verified | BOQ shorthand: IDM+ 18A/64D. 6U rackmount. Weight 23 kg. Two 9-channel analog blocks. Suitable for 5–8 feeder substations.
PROD_PF_DFR_05 | IDM+ 36 | PF_DFR | Digital Fault / Disturbance Recorder | DFR_DDR_001; PMU_001; FAULT_LOC_001; PQ_CLASSA_001 | Substation / feeder / plant bus | IDM+ 36: 36 analog and 128 digital channels (6U, 19-inch rack). Largest standard IDM+ variant for substations with many feeders. Same optional functions (PMU, TWS, Class A PQ). | IEEE C37.118-2014; IEC 61000-4-30 Class A; IEC 61850 | IEC 61850; IEC 60870-5-104; DNP 3.0; Modbus | QR_DFR_001 |  | GPS antenna; IRIG-B; TWS card (optional) | https://www.qualitrolcorp.com/products/IDMPlus | Verified via Tavily web research + Gemba Samples BOQ/product manuals. | Verified | BOQ shorthand: IDM+ 36A/128D (or IDM+ 36A/64D for 64-DI variant). 6U rackmount. Four 9-channel analog blocks. Suitable for 10–12 feeder substations.
PROD_PF_TWS_04 | TWS FL-8 | PF_TWS | Traveling Wave Fault Locator | FAULT_LOC_001 | Transmission line / feeder | Modular traveling wave fault locator monitoring 2, 4, 6 or 8 lines using double-ended method with GPS time synchronization | IEC 61850 GOOSE; IEEE, EU and IEC immunity | Ethernet (RJ45/fiber), RS-232, RS-485, PSTN/GSM modem, IEC 61850 GOOSE, NTP | QR_FAULT_LOC_001 | Linear couplers (LC); GPS antenna and cable | iQ+ software | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'The_Power_Grid\TWS_FL_1016871a.pdf'; verify before quoting.
PROD_PF_TWS_05 | TWS FL-1 | PF_TWS | Traveling Wave Fault Locator | FAULT_LOC_001 | Transmission line / feeder | Fixed-format traveling wave fault locator monitoring one line, for distributed substations, using double-ended method with GPS time synchronization | IEC 61850 GOOSE; IEEE, EU and IEC immunity | Ethernet (RJ45/fiber), RS-232, RS-485, PSTN/GSM modem, IEC 61850 GOOSE, NTP | QR_FAULT_LOC_001 | Linear couplers (1 set); GPS antenna |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'The_Power_Grid\TWS_FL_1016871a.pdf'; verify before quoting.
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | Power Quality Recorder | PQ_CLASSA_001; RENEWABLE_PCC; DATA_CENTER_POWER | PCC / bus / feeder | Performance measuring and monitoring device combining IEC 61000-4-30 Class A power quality, digital fault recording and energy metering. 9 (optional 18/27/36) analog channels available as AC or DC. | IEC 61000-4-30 Class A (Edition 2.0); EN 50160; IEC 61000-3-6; IEC 61000-3-7; IEC 60255-22-6; IEC 61000-4-3/4/5/6/8/12; CISPR-11 | Ethernet; RS232; USB | QR_PQ_001 |  | GPS time sync module | Preparation/Qualitrol Product/The_Power_Grid/Informa_PQ_17eb70e4.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'The_Power_Grid\Informa_PQ_17eb70e4.pdf'; verify before quoting.
PROD_PF_PMU_04 | IDM+ (PMU option) | PF_PMU | Phasor Measurement Unit | PMU_001; DFR_DDR_001; WAMS_001 | Transmission grid measurement point / substation bus / feeder | IDM+ with PMU option enabled: provides synchrophasor streaming per IEEE C37.118-2014 alongside full DFR/DDR functions. Available in 9, 18, or 36 analog channel variants. Used in FMS+WAMS deployments across GCC and international utilities. | IEEE C37.118-2014; IEC 61850; IEC 61000-4-30 Class A | IEC 61850 GOOSE; DNP 3.0; Modbus TCP; C37.118 streaming | QR_PMU_001 | GPS antenna; iQ+ Master Station software |  | https://www.qualitrolcorp.com/products/IDMPlus | Verified via Tavily web research + Gemba Samples BOQ/product manuals. | Verified | PMU is an optional add-on license/card for IDM+ 9/18/36. Reporting rates: 25 or 50 fps at 50 Hz; 30 or 60 fps at 60 Hz (typical). Used by GCCIA, OETC, Scottish Power, Statnett, EGAT, etc.
PROD_PDF_ISGM | iSGM | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Online intelligent, distributed SF6 gas density monitoring system for gas insulated assets; jointly developed by Qualitrol and Wika; DIN rail mounted acquisition nodes with SMARTSUB CBM software. | NERC CIP | DNP 3.0; IEC 61850; SCADA; PI Historian | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Breakers/iSGM_dde77d65.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Breakers\iSGM_dde77d65.pdf'; verify before quoting.
PROD_PDF_QBCM_QUALITROL_BREAKER_CONDITION_MONITORING | QBCM (Qualitrol Breaker Condition Monitoring) | PF_BREAKER | Circuit Breaker Monitor | BRK_HEALTH_001 | Circuit breaker | Breaker condition monitor available in QBCM-LT, QBCM-ST and QBCM-IP configurations; monitors SF6, trip/close coils, main contacts, motors and heaters with fingerprinting and cloning. | IEC 60255-21-1, -2; IEC60255-27; EN61000-6-5; EN55011 Class A | DNP3.0, IEC 61850, Modbus | QR_BRK_001 |  |  | Preparation/Qualitrol Product/Breakers/QBCM_9a27f030.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Breakers\QBCM_9a27f030.pdf'; verify before quoting.
PROD_PDF_AKM_38750_38920_38960 | AKM 38750/38920/38960 | PF_BREAKER | Circuit Breaker Monitor | BRK_HEALTH_001 | Circuit breaker | SF6 gas density monitors providing mechanical local indication with automatic temperature compensation and optional alarm/limit control switches for gas insulated circuit breakers, switchgear and transformers. | IP54 (NEMA 3S); ANSI/IEEE C37.90; UL; CSA | Optional transmitter for remote/analog/SCADA indication | QR_BRK_001 |  |  | Preparation/Qualitrol Product/Breakers/SF6_Gas_Density_Gauges_0d311061.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Breakers\SF6_Gas_Density_Gauges_0d311061.pdf'; verify before quoting.
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Modular transformer monitoring system for condition based online monitoring; interfaces with Qualitrol and third party sensors for main tank, LTC, cooling, bushing, DGA, PD and fiber optic monitoring. | IEC 60255-5:2000; IEEE C37.90-2005; C37.90.3; IEC 61000-4 series; EN 55011 Class A; IEC 60529:2001; IEC 60068 series; IEEE/IEC health algorithm standards | DNP 3.0 (Level 3), Modbus, IEC 61850, IEC 60870-104-5 | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Bushings\QTMS_b041f478.pdf'; verify before quoting.
PROD_PDF_QUALITROL_DMS_GEN3_GEN3_PDMS | Qualitrol DMS Gen3 (Gen3 PDMS) | PF_GIS_PD | GIS PD Monitor | GIS_PD_001 | GIS bay | Fully integrated UHF partial discharge monitoring system for Gas Insulated Switchgear with proprietary ANN classification into six GIS defect types. | IEC 61850; Industrial Generic Immunity and Industrial Emission EMC standards | Modbus; DNP 3.0; IEC 61850 (copper or fiber) | QR_GIS_PD_001 |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/Gen_3_PDM_c5bdb2c6.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Gas_Insulated_Switchgear\Gen_3_PDM_c5bdb2c6.pdf'; verify before quoting.
PROD_PDF_QUALITROL_QPDM_SERIES | Qualitrol QPDM Series | PF_PD_TRANSFORMER | Transformer PD Monitor | TR_PD_001 | Power transformer | Continuous online UHF partial discharge monitoring system for transformers and small GIS, supporting up to 6 UHF sensors with ANN-based analysis and remote client software. | IEEE C37.98; BS EN60068-2-2/-2-1/-2-78; BS EN55022; BS EN61000 series; IEC 60255-5; IEC 61180-1; CE; RoHS | IEC 61850; Modbus; Ethernet (fiber optic or RJ45) | QR_TR_PD_001 |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/QPDM_Software_fad2476a.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Gas_Insulated_Switchgear\QPDM_Software_fad2476a.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_AGTRACII | Iris Power AGTracII | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Continuous on-line air gap monitoring system for hydro generators using capacitive sensors, with real-time analysis, alarm management, trending and protective functionality. |  | SCADA | QR_GEN_AIRGAP_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/AGTracII_6cebaaf2.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\AGTracII_6cebaaf2.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_CAPACITIVE_AIR_GAP_SENSOR_CGS020210_CGP_02 | Iris Power Capacitive Air Gap Sensor CGS020210 (CGP-02) | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Capacitive air gap probe for continuous on-line air gap monitoring in hydro generators, with linearization module. |  |  | QR_GEN_AIRGAP_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\Capacitive_Air_Gap_Sensor_d4fb14ac.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_CAPACITIVE_AIR_GAP_SENSOR_CGS020310_CGP_03 | Iris Power Capacitive Air Gap Sensor CGS020310 (CGP-03) | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Capacitive air gap probe for continuous on-line air gap monitoring in hydro generators. |  |  | QR_GEN_AIRGAP_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\Capacitive_Air_Gap_Sensor_d4fb14ac.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_CAPACITIVE_AIR_GAP_SENSOR_CGS020410_CGP_04 | Iris Power Capacitive Air Gap Sensor CGS020410 (CGP-04) | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Capacitive air gap probe for continuous on-line air gap monitoring in hydro generators. |  |  | QR_GEN_AIRGAP_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\Capacitive_Air_Gap_Sensor_d4fb14ac.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_CGL_LINEARIZATION_MODULE | Iris Power CGL Linearization Module | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Linearization module converting capacitive gap sensor output to 4-20mA or 2-10V industrial format for continuous monitoring. |  | 4-20mA; 2-10V | QR_GEN_AIRGAP_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\Capacitive_Air_Gap_Sensor_d4fb14ac.pdf'; verify before quoting.
PROD_PDF_PDTECH_DELTAMAXX | PDTech DELTAMAXX | PF_GEN_PD | Generator PD Monitor | GEN_PD_001 | Generator | Ultra-compact digital dissipation factor/capacitance analyzer with optional partial discharge detector for test voltages up to 50 kV, for generator/motor windings, dry-type transformers, capacitors and cables. | IEC 60034-27-3, IEEE 286, IEC 60034-27-1, IEC 60270, IEEE 1434 | USB | QR_GEN_PD_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/DeltaMaxx_Analyzer_6ea453b9.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\DeltaMaxx_Analyzer_6ea453b9.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_EL_CID_EVOLUTION | Iris Power EL CID Evolution | PF_GEN_PD | Generator PD Monitor | GEN_PD_001 | Generator | Low-flux core tester for detecting stator core inter-laminar insulation faults in turbine generators, hydrogenerators, and large motors. |  |  | QR_GEN_PD_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/EL_CID_8fe18258.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\EL_CID_8fe18258.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_EPOXY_MICA_CAPACITORS_EMC_80_PF | Iris Power Epoxy Mica Capacitors (EMC) 80 pF | PF_GEN_PD | Generator PD Monitor | GEN_PD_001 | Generator | Epoxy Mica Capacitor PD sensors for detecting stator winding partial discharge in motors, generators and bus; permanently installed at least one per phase. | IEC TS 60034-27-2; IEEE 1434; IEEE 323-1983; ASTM D1868; IEC 60270; ASTM D2303-85; IEC 60112; IEEE 1043; IEEE 930-1987 |  | QR_GEN_PD_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/Epoxy_Mica_Capacitors_(EMC_Sensors)_8912f79b.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\Epoxy_Mica_Capacitors_(EMC_Sensors)_8912f79b.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_EVAII | Iris Power EVAII | PF_GEN_EWV | Generator End-Winding Vibration Monitor | GEN_EWV_001 | Generator | Fiber optic endwinding vibration accelerometer for motor and generator stator endwindings; single or dual axis; air-cooled or hydrogen-cooled kits. | IEC 60034-32; ISO 16063-21 |  | QR_GEN_EWV_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/EVAII_Endwinding_Vibration_Monitoring_3333c33c.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\EVAII_Endwinding_Vibration_Monitoring_3333c33c.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_FLUXTRACII_R_4208 | Iris Power FluxTracII-R 4208 | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Third generation continuous on-line rotor magnetic flux monitoring system to detect shorted rotor turns in 2 and 4 pole round rotor motors and turbogenerators. |  | Modbus TCP/IP; USB; Ethernet | QR_GEN_AIRGAP_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-R_4208_60a9f974.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\FluxTracII-R_4208_60a9f974.pdf'; verify before quoting.
PROD_PDF_FLUXTRACII_S_4208 | FluxTracII-S 4208 | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Continuous on-line rotor flux monitor for rotor winding shorted turn detection in salient pole machines such as hydro generators, motorgenerators in reversible pump-turbines, and salient pole motors. |  | Modbus TCP/IP; USB; Ethernet | QR_GEN_AIRGAP_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-S_4208_39a21cdd.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\FluxTracII-S_4208_39a21cdd.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_MDSP3 | Iris Power MDSP3 | PF_MOTOR | Motor Monitor | MTR_PD_001; MTR_TEMP_001 | Large motor | Portable Motor Digital Signal Processor using Current Signature Analysis to detect broken rotor bars, cage winding faults and air gap eccentricity in squirrel cage induction motors. | ISO 20958:2013 | USB | QR_MOTOR_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/MDSP3_aee0c628.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\MDSP3_aee0c628.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_PDA_IV | Iris Power PDA-IV | PF_GEN_PD | Generator PD Monitor | GEN_PD_001 | Generator | Periodic on-line partial discharge monitoring instrument for hydro generators; portable instrument with noise separation via pulse shape and time of arrival. | IEEE Std. 1434-2014; IEC60034-27-2:2012; IEC 60068-2-6; IEC 60068-2-27; MIL-STD 810G; CE; UL | USB; Ethernet | QR_GEN_PD_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDA-IV_e8515c86.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\PDA-IV_e8515c86.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_PDTRACII_4208 | Iris Power PDTracII 4208 | PF_MOTOR | Motor Monitor | MTR_PD_001; MTR_TEMP_001 | Large motor | Continuous online partial discharge monitoring system for motors, generators, dry-type transformers and air-insulated switchgear rated up to 35 kV, using three 80 pF capacitive couplers. | IEEE 1434:2016; IEC 60034-27-2:2012; IEC 62478 | Modbus over Ethernet (TCP/IP); USB | QR_MOTOR_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDTracII_08f5c95a.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\PDTracII_08f5c95a.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_CORONA_PROBE_MODEL_PPM_97 | Iris Power Corona Probe Model PPM-97 | PF_GEN_PD | Generator PD Monitor | GEN_PD_001 | Generator | Portable, battery operated instrument for off-line detection and location of partial discharge in HV rotating machine stator windings (also known as TVA Probe). |  |  | QR_GEN_PD_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/PPM-97_Corona_Probe_9c7539d3.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\PPM-97_Corona_Probe_9c7539d3.pdf'; verify before quoting.
PROD_PDF_QCM_PPDM | QCM-PPDM | PF_PD_TRANSFORMER | Transformer PD Monitor | TR_PD_001 | Power transformer | Portable partial discharge monitor for transformers and GIS; touch screen based, field operated UHF PD system for online/offline PD testing. | IEEE C37.98; BS EN60068 series; BS EN55022; BS EN61000 series; IEC 60255-5; IEC 61180-1 | Ethernet (RJ45 10/100 Mbps); USB; NTP/SNTP; optional GPRS | QR_TR_PD_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/QPPDM_2ca3bb9a.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\QPPDM_2ca3bb9a.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_RFAII_R | Iris Power RFAII-R | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Portable on-line rotor flux analyzer to detect shorted rotor turns in round rotor motors and turbogenerators (up to 4 poles). |  | USB, Ethernet | QR_GEN_AIRGAP_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/RFAII-R_c16db884.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\RFAII-R_c16db884.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_RFAII_S | Iris Power RFAII-S | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | GEN_AIRGAP_001 | Hydro generator | Portable on-line rotor flux analyzer to detect shorted rotor turns in salient pole motors and hydro generators (RFAII-S). |  | USB (type B), Ethernet (RJ45) | QR_GEN_AIRGAP_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/RFAII-S_551dd1fa.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\RFAII-S_551dd1fa.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_RIV_800 | Iris Power RIV 800 | PF_GEN_PD | Generator PD Monitor | GEN_PD_001 | Generator | Magnetically supported Robotic Inspection Vehicle for stator core interlaminar insulation testing (EL CID) and visual inspection of generator/motor stator and rotor. |  |  | QR_GEN_PD_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/Robotic_Inspection_Vehicle_&_Camera_System_5c0af922.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\Robotic_Inspection_Vehicle_&_Camera_System_5c0af922.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_STATOR_SLOT_COUPLERS_SSC | Iris Power Stator Slot Couplers (SSC) | PF_GEN_PD | Generator PD Monitor | GEN_PD_001 | Generator | Sensors designed to detect stator winding partial discharge activity in operating gas or steam turbine generators, installed under stator bar winding wedges or between top and bottom bars. | NEMA FR4 (Class F); NEMA FR5 (Class H); ATEX certified available on request |  | QR_GEN_PD_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/Stator_Slot_Couplers_(SSC)_bb887587.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\Stator_Slot_Couplers_(SSC)_bb887587.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_SWA_STATOR_WEDGE_ANALYZER | Iris Power SWA (Stator Wedge Analyzer) | PF_MOTOR | Motor Monitor | MTR_PD_001; MTR_TEMP_001 | Large motor | Handheld instrument to assess tightness of stator wedges in motors or generators using an automated tapping probe and accelerometer, presenting numeric values and a color-coded tightness map. |  |  | QR_MOTOR_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/Stator_Wedge_Analyzer_(SWA)_ea20c256.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\Stator_Wedge_Analyzer_(SWA)_ea20c256.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_TGA_B | Iris Power TGA-B | PF_GEN_PD | Generator PD Monitor | GEN_PD_001 | Generator | Portable periodic on-line partial discharge monitoring instrument for motors and turbine generators using busbar installed EMCs | IEEE Std. 1434-2014, IEEE Std.1129, IEC 60034-27-2:2012 | USB, Ethernet | QR_GEN_PD_001 |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-B_b099cbd2.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Generator_Solutions\TGA-B_b099cbd2.pdf'; verify before quoting.
PROD_PDF_QUALITROL_CORE_PACKAGE | Qualitrol Core Package | PF_DGA | Online DGA Monitor | TR_DGA_001 | Oil-filled transformer | Entry-tier transformer condition-based monitoring package with single-gas (hydrogen) DGA, QTMS temperature monitoring and APM software covering common transformer failure modes. | IEC-61850; NERC; IEC; NIST cyber security standards | IEC-61850, ModBUS, DNP3.0 | QR_TR_DGA_001 |  |  | Preparation/Qualitrol Product/Software_Solutions/Core_Package_02229adb.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Software_Solutions\Core_Package_02229adb.pdf'; verify before quoting.
PROD_PDF_PDTECH_DRA_3 | PDTech DRA-3 | PF_GEN_PD | Generator PD Monitor | GEN_PD_001 | Generator | Dielectric Response Analyzer for off-line insulation diagnosis of generator and motor windings; also applicable to transformers. Measures charging/discharging (polarization/depolarization) currents (PDC). | IEEE 43 | USB | QR_GEN_PD_001 |  |  | Preparation/Qualitrol Product/Software_Solutions/DRA3_Software_3041882e.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Software_Solutions\DRA3_Software_3041882e.pdf'; verify before quoting.
PROD_PDF_QUALITROL_SMARTSUB | Qualitrol SmartSUB | PF_SOFTWARE | Monitoring Software / Asset Platform | SUB_SOFT_001; COMM_SCADA_001 | Multi-asset / site / fleet | Asset Performance Management Software with Monitoring, Analytics, and Maintenance modules for substation multi-asset condition monitoring and predictive maintenance. | IEEE; IEC; CIGRE; CIS Benchmarks; NERC CIP; NIST SP 800; IEC 62443 | IEC-61850; IEC-61870; DNP3.0; MODBUS | QR_SOFT_001 |  |  | Preparation/Qualitrol Product/Software_Solutions/SmartSUB_342941d3.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Software_Solutions\SmartSUB_342941d3.pdf'; verify before quoting.
PROD_PDF_IRIS_POWER_DCR_60_2 | Iris Power DCR 60-2 | PF_GEN_PD | Generator PD Monitor | GEN_PD_001 | Generator | Off-line DC ramp test set to identify problems in stator groundwall insulation of large AC electric machines | IEEE Standard 95-2002; EN61326 (EMC); Bureau of Reclamation Report REC-ERC-78-7 | USB (PC connection) | QR_GEN_PD_001 |  |  | Preparation/Qualitrol Product/The_Power_Grid/DCR_60_4ae9ab6d.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'The_Power_Grid\DCR_60_4ae9ab6d.pdf'; verify before quoting.
PROD_PDF_QUALITROL_015_VERTICAL_OIL_LEVEL_INDICATOR | Qualitrol 015 Vertical Oil Level Indicator | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Mechanical oil (liquid) level indicator with adjustable contacts (switches) for low oil level alarming; magnetic couple minimizes leak paths; optional gas sampling valve. | IP55; NEMA 3R; ISO 228/1; UL; CSA |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/015_Vertical_Oil_Level_Indicator_fb43241e.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\015_Vertical_Oil_Level_Indicator_fb43241e.pdf'; verify before quoting.
PROD_PDF_QUALITROL_020_030_AKM_46969 | Qualitrol 020/030 & AKM 46969 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Small oil level indicators providing continuous indication of liquid level inside transformer main tank, conservator tank or load tap changer compartment. |  |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/020_Small_Oil_Level_Indicator_00ef7115.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\020_Small_Oil_Level_Indicator_00ef7115.pdf'; verify before quoting.
PROD_PDF_QUALITROL_029_VERTICAL_OIL_LEVEL_INDICATOR | Qualitrol 029 Vertical Oil Level Indicator | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Vertical oil level indicator providing continuous indication of liquid level in transformer main tank, conservator tank or load tap changer compartment; gear driven mechanism with weld-on flange. |  |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/029_Subway_Oil_Level_Indicator_8f7dd70b.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\029_Subway_Oil_Level_Indicator_8f7dd70b.pdf'; verify before quoting.
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Large oil level indicators providing continuous indication of liquid level inside transformer main tank, conservator tank or LTC compartment; gear or lever driven float mechanisms with integrated switches for alarm/limit control. | UL listed class 1 div 2 (045 models) | 4-20mA or 0-1mA analog output | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf'; verify before quoting.
PROD_PDF_QUALITROL_035_LIQUID_LEVEL_CONTROL_GAUGE | QUALITROL 035 Liquid Level Control Gauge | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Flange mounted liquid level gauge providing continuous indication of oil level inside transformer main tank, conservator tank or load tap changer compartment with integrated limit and alarm switches. |  |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/035_Flange_Mounted_Liquid_Level_Gauge_3a00eded.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\035_Flange_Mounted_Liquid_Level_Gauge_3a00eded.pdf'; verify before quoting.
PROD_PDF_QUALITROL_038_GAS_ACCUMULATION_INDICATOR | QUALITROL 038 Gas Accumulation Indicator | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Mechanical measurement of gas accumulation within a conservator style transformer with alarm functions and integrated sampling port for laboratory gas analysis. | IP54 |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/038_Gas_Accumulation_Indicator_a3362790.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\038_Gas_Accumulation_Indicator_a3362790.pdf'; verify before quoting.
PROD_PDF_QUALITROL_032_042_045 | QUALITROL 032/042/045 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Large oil level indicators providing continuous indication of liquid level inside a transformer's main tank, conservator tank or load tap changer compartment. Models with gear (042/045) or lever (032) driven float mechanisms. | UL listed for Class 1 Div 2 (045 models) | 4-20mA or 0-1mA analog output | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf'; verify before quoting.
PROD_PDF_QUALITROL_AKM_44712_34725 | QUALITROL AKM 44712/34725 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Large oil level indicators with M50 thread mount; gear (34725) or lever (44712) driven float mechanisms for transformer oil level monitoring. |  | 4-20mA analog output | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf'; verify before quoting.
PROD_PDF_QUALITROL_049 | Qualitrol 049 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Vertical oil level switches providing continuous indication of liquid level within an oil filled transformer main tank, conservator tank or LTC compartment, with integrated limit and alarm switch functions. | UL; CSA; DIN 259; DIN 40430 |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/049_Vertical_Oil_Level_Indicator_b0a06108.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\049_Vertical_Oil_Level_Indicator_b0a06108.pdf'; verify before quoting.
PROD_PDF_QUALITROL_050 | Qualitrol 050 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Pressure and/or vacuum indicator for accurate representation of pressure state inside a vessel; 3.5 inch dial with at least 180° deflection. For pressure/vacuum indication on transformers and related equipment. |  |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/050_PressureVacuum_Gauge_and_Bleeders_940edfee.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\050_PressureVacuum_Gauge_and_Bleeders_940edfee.pdf'; verify before quoting.
PROD_PDF_QUALITROL_070_SERIES_PRESSURE_VACUUM_BLEEDER | QUALITROL 070 Series Pressure-Vacuum Bleeder | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Pressure-vacuum bleeder with local indication dial for balancing pressure and vacuum in sealed transformer vessels. | ANSI standards for transformers |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/070_PressureVacuum_Gauge_and_Bleeders_36edcc50.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\070_PressureVacuum_Gauge_and_Bleeders_36edcc50.pdf'; verify before quoting.
PROD_PDF_QUALITROL_351_SERIES_PRESSURE_VACUUM_BLEEDER | QUALITROL 351 Series Pressure-Vacuum Bleeder | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Pressure-vacuum bleeder for balancing pressure and vacuum in sealed transformer vessels, with top/bottom/side mounting. | ANSI standards for transformers |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/070_PressureVacuum_Gauge_and_Bleeders_36edcc50.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\070_PressureVacuum_Gauge_and_Bleeders_36edcc50.pdf'; verify before quoting.
PROD_PDF_QUALITROL_092_FLOW_INDICATORS | QUALITROL 092 Flow Indicators | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Flow indicator designed to indicate pump on/off conditions within a forced cooling system; select models indicate flow direction; up to 2 SPST/SPDT switches for control/alarm. | UL/CSA recognized; IP66/IP54 |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/092_Flow_Gauge_13c5e971.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\092_Flow_Gauge_13c5e971.pdf'; verify before quoting.
PROD_PDF_QUALITROL_104_TR6000_REMOTE_MOUNT_THERMOMETERS | QUALITROL 104/TR6000 Remote Mount Thermometers | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Capillary based, remote indicating mechanical thermometer with bourdon tube measurement, resettable maximum pointer and up to 4 switches for oil or simulated winding temperature. |  | SCADA analog outputs (0-1 mA and 4-20 mA) | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/104TR6000_Remote_Temperature_Indicator_5d6da65e.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\104TR6000_Remote_Temperature_Indicator_5d6da65e.pdf'; verify before quoting.
PROD_PDF_QUALITROL_105_REMOTE_MOUNT_THERMOMETER | QUALITROL 105 Remote Mount Thermometer | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Capillary based, remote indicating mechanical thermometer with bourdon tube measurement, resettable maximum pointer and up to 3 switches for temperature alarms and control, used to measure oil or simulated winding temperature. | UL and CSA recognized switches; ISO 9001 |  | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/105_Remote_Mount_Thermometer_b568f343.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\105_Remote_Mount_Thermometer_b568f343.pdf'; verify before quoting.
PROD_PDF_QUALITROL_120 | Qualitrol 120 | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Side mounting bourdon tube direct mount thermometer with 6" dial face, resettable maximum temperature pointer and up to 4 adjustable switches for control and alarm functions. | UL recognized; CSA certified switches |  | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/120_Bourdon_Tube_Thermometer_a5e8092f.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\120_Bourdon_Tube_Thermometer_a5e8092f.pdf'; verify before quoting.
PROD_PDF_QUALITROL_130 | QUALITROL 130 | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Winding temperature simulation system with one well and up to two RTDs for remote indication and SCADA | DIN 42554; DIN 40050 IP54; NEMA 3R | RTD output (Pt100 / Cu10); optional 4-20 mA via PT100 converter | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/130_Thermal_Plate_0dbe066d.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\130_Thermal_Plate_0dbe066d.pdf'; verify before quoting.
PROD_PDF_QUALITROL_THERMAL_PLATE | QUALITROL Thermal Plate | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Winding temperature simulation system with up to three wells and heating elements for winding/oil temperature monitoring | IP54 / NEMA 3R (system); ISO 9001 | Accepts probes, capillaries, or RTD temperature sensing devices | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/130_Thermal_Plate_0dbe066d.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\130_Thermal_Plate_0dbe066d.pdf'; verify before quoting.
PROD_PDF_QUALITROL_141 | QUALITROL 141 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Pressure or vacuum switch providing operating control, limit or alarm functions for transformers and load tap changers. | UL, CSA listed |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_47500_Pressure_Control_Switches_1068660c.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\AKM_47500_Pressure_Control_Switches_1068660c.pdf'; verify before quoting.
PROD_PDF_QUALITROL_146 | QUALITROL 146 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Compact pressure or vacuum switch for control panel integration. | UL, CSA listed |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_47500_Pressure_Control_Switches_1068660c.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\AKM_47500_Pressure_Control_Switches_1068660c.pdf'; verify before quoting.
PROD_PDF_QUALITROL_148 | QUALITROL 148 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Pressure or vacuum switch with optional indication dial for transformers and LTCs. | UL, CSA listed |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_47500_Pressure_Control_Switches_1068660c.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\AKM_47500_Pressure_Control_Switches_1068660c.pdf'; verify before quoting.
PROD_PDF_QUALITROL_AKM_35600 | QUALITROL AKM 35600 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Weatherproof pressure or vacuum switch with fast reaction and optional lockable test valve. | UL, CSA |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/148_PressureVacuum_Switch_2a33e83a.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\148_PressureVacuum_Switch_2a33e83a.pdf'; verify before quoting.
PROD_PDF_QUALITROL_47500 | Qualitrol 47500 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Pressure or vacuum switch series with multiple tank connection options | UL, CSA |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\141_PressureVacuum_Switch_aefd2f72.pdf'; verify before quoting.
PROD_PDF_QUALITROL_150_151_DIRECT_MOUNT_THERMOMETERS | QUALITROL 150/151 Direct Mount Thermometers | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Side mounting bi-metal thermometers with temperature indication and resettable maximum temperature pointer, 4 inch dial, for transformer and related electrical apparatus. |  |  | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/150151_Indication_Only_Temperature_Indicator_99461e24.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\150151_Indication_Only_Temperature_Indicator_99461e24.pdf'; verify before quoting.
PROD_PDF_QUALITROL_165_167 | QUALITROL 165/167 | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Side mounted bi-metal direct mount thermometers with temperature indication, resettable maximum pointer and up to 3 control/alarm switches. |  |  | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\165167_Direct_Temperature_Indicator_cb96e6da.pdf'; verify before quoting.
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Direct mount bi-metal thermometer with temperature indication, resettable maximum pointer and 2 control/alarm switches. |  |  | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_47080_Direct_Mount_Bimetal_Thermometer_1a28ed38.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\AKM_47080_Direct_Mount_Bimetal_Thermometer_1a28ed38.pdf'; verify before quoting.
PROD_PDF_QUALITROL_201_SERIES | Qualitrol 201 Series | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Small pressure relief device providing overpressure protection on transformers and liquid filled apparatus, resealing automatically. | ANSI C57.12.20.2007 |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/201_Pressure_Relief_Valves_d1b1429e.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\201_Pressure_Relief_Valves_d1b1429e.pdf'; verify before quoting.
PROD_PDF_QUALITROL_202_SERIES | Qualitrol 202 Series | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Small pressure relief device with indicator for overpressure protection on transformers. | ANSI C57.12.20.2007 |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/201_Pressure_Relief_Valves_d1b1429e.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\201_Pressure_Relief_Valves_d1b1429e.pdf'; verify before quoting.
PROD_PDF_QUALITROL_205_SERIES | Qualitrol 205 Series | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Small pressure relief device with greater flow rate and adjustable pressure rating for overpressure protection. | ANSI C57.12.20.2007 |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/201_Pressure_Relief_Valves_d1b1429e.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\201_Pressure_Relief_Valves_d1b1429e.pdf'; verify before quoting.
PROD_PDF_QUALITROL_206 | Qualitrol 206 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Medium pressure relief device providing mechanical overpressure protection on transformers, load tap changers and other liquid-filled apparatus; self-resealing with optional shield and up to two sealed switches. |  |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/206_Medium_Pressure_Relief_Device_(MPRD)_8039338a.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\206_Medium_Pressure_Relief_Device_(MPRD)_8039338a.pdf'; verify before quoting.
PROD_PDF_QUALITROL_070_351_PRESSURE_VACUUM_BLEEDERS | QUALITROL 070/351 Pressure-Vacuum Bleeders | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Pressure-vacuum bleeders designed to balance pressure and vacuum conditions within a sealed vessel by releasing or admitting air and gas, for transformers, conservator tanks and load tap changers. | ANSI standards for transformers |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/351_PressureVacuum_Gauge_and_Bleeders_724e62e8.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\351_PressureVacuum_Gauge_and_Bleeders_724e62e8.pdf'; verify before quoting.
PROD_PDF_QUALITROL_T_GUARD_408 | Qualitrol T/Guard 408 | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Multi-channel fiber optic real-time hot spot temperature monitoring system for dry-type and oil-filled transformers, using Qualitrol T2 GaAs fiber optic probes. | IEC 61000-4 series; IEC 61180; FCC 47 CFR Part 15 Sub B; CISPR 11; EN 61010-1:2010; Directive 2014/35/EU; Directive 2014/30/EU; Directive 2011/65/EU RoHS | ASCII; Modbus RTU; DNP 3.0 (optional) | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf'; verify before quoting.
PROD_PDF_QUALITROL_T_GUARD_408XT | Qualitrol T/Guard 408XT | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Ethernet/Smart Grid ready version of the 408 fiber optic winding temperature monitoring system with web server and IEC 61850 support. | IEC 61000-4 series; IEC 61180; FCC 47 CFR Part 15 Sub B; CISPR 11; EN 61010-1:2010; Directive 2014/35/EU; Directive 2014/30/EU; Directive 2011/65/EU RoHS | ASCII; Modbus RTU; DNP 3.0; HTTP; Modbus over Ethernet; IEC 60870-5-104; IEC 61850 | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf'; verify before quoting.
PROD_PDF_QUALITROL_900_RPRR | QUALITROL 900 RPRR | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Mechanical rapid pressure rise relay for oil space transformer protection, detecting sudden pressure changes. | UL (accessory seal-in relay Class 1, Div 2) |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf'; verify before quoting.
PROD_PDF_QUALITROL_910_RPRR | QUALITROL 910 RPRR | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Mechanical rapid pressure rise relay for gas space transformer protection, detecting sudden pressure changes. | UL (accessory seal-in relay Class 1, Div 2) |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf'; verify before quoting.
PROD_PDF_QUALITROL_909_300_01 | Qualitrol 909-300-01 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Seal-in relay that captures and maintains momentary/fast-acting contact closures; used with 900/910 Rapid Pressure Rise Relays. | UL508; VDE 0435, 0631, 0700, 0860; UL873; CSA 22.2 No.14 |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/909_Seal-In_Relay_a0e59e43.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\909_Seal-In_Relay_a0e59e43.pdf'; verify before quoting.
PROD_PDF_QUALITROL_909_300_02 | Qualitrol 909-300-02 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Seal-in relay listed for UL1604 class I division II hazardous locations; captures fast-acting contact closures. | UL508; UL1604 (class I, div II hazardous locations); VDE 0435, 0631, 0700, 0860; UL873; CSA 22.2 No.14 |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/909_Seal-In_Relay_a0e59e43.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\909_Seal-In_Relay_a0e59e43.pdf'; verify before quoting.
PROD_PDF_QUALITROL_930 | Qualitrol 930 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Multi-function electronic pressure monitor with adjustable pressure sensitive sensors for rapid pressure rise detection and static pressure monitoring/control, with SCADA outputs and optional multi-sensor logic. | ANSI/IEEE C37.90 | 0-1 mA / 4-20 mA analog output; SCADA | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/930_Electronic_Pressure_Monitor_f58007ab.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\930_Electronic_Pressure_Monitor_f58007ab.pdf'; verify before quoting.
PROD_PDF_QUALITROL_AKM345_GEN3_OTIWTI | Qualitrol AKM345 Gen3 OTIWTI | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Oil and winding temperature indicator for transformers using bellows technology with integrated winding temperature simulation. | ISO 12944 (C5-High); IEC 60076-22-1; Category III, Pollution degree 2, Insulation Class 1 | RS-485 Modbus | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM345_Gen3_Oil_and_Winding_Temperature_Indicator_09e05650.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\AKM345_Gen3_Oil_and_Winding_Temperature_Indicator_09e05650.pdf'; verify before quoting.
PROD_PDF_AKM_44611_48471 | AKM 44611/48471 | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Top mounting bi-metal thermometers with temperature indication and resettable maximum temperature pointer for direct mount applications. | IEC 529 IP54; NEMA 3S |  | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_4461148471_Bi-Metal_Thermometer_71abb218.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\AKM_4461148471_Bi-Metal_Thermometer_71abb218.pdf'; verify before quoting.
PROD_PDF_AKM_44612_44622_44617_44618_44650 | AKM 44612/44622/44617/44618/44650 | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Direct mount thermometers for indication of oil (liquid) or winding temperature in power transformers, with resettable maximum temperature pointer and up to 2 integrated switches for alarm and control, optional Pt100 SCADA output. | IEC 529 | Optional SCADA (Pt100) output | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_44612446224461744618_Thermometer_188b5fee.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\AKM_44612446224461744618_Thermometer_188b5fee.pdf'; verify before quoting.
PROD_PDF_QUALITROL_032_042_045_LARGE_OIL_LEVEL_INDICATOR | Qualitrol 032/042/045 Large Oil Level Indicator | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Large oil level indicators providing continuous indication of liquid level inside transformer main tank, conservator tank or load tap changer compartment; gear (042/045) or lever (032) driven float mechanisms with integrated switches for limit/alarm. | UL listed Class 1 Div 2 (045 models) | 4-20mA / 0-1mA analog output (with 039 Remote Enclosure) | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/045_Liquid_Level_Gauge_09f522e9.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\045_Liquid_Level_Gauge_09f522e9.pdf'; verify before quoting.
PROD_PDF_QUALITROL_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATOR | QUALITROL AKM 44712 / 34725 Large Oil Level Indicator | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Large oil level indicator with gear (34725) or lever (44712) float mechanism for monitoring transformer liquid level. |  | 4-20mA analog output (SCADA) | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\AKM_Oil_Level_Indicator_65d66203.pdf'; verify before quoting.
PROD_PDF_AKM_OLR | AKM OLR | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Hydro-mechanical, capillary based remote oil level indicator with integrated microswitches for control and alarm functions; electronic 4-20mA output available for SCADA integration. | DIN 40050 IP54 | 4-20mA analog output; Pt100; Cu10 voltage outputs for SCADA integration | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_OLR_Remote_Mechanical_Oil_Level_Indicator_ad31eee0.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\AKM_OLR_Remote_Mechanical_Oil_Level_Indicator_ad31eee0.pdf'; verify before quoting.
PROD_PDF_QUALITROL_KIT_930 | QUALITROL KIT-930 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Complete field test kit for confidence testing of QUALITROL 930 Electronic pressure monitor, including components, tools and power supplies in a rugged carrying case. | EN55011, EN61000-4-2, EN61000-4-3, EN61000-4-4, EN61000-4-5, EN61000-4-6, EN61000-4-8, EN61000-4-11, EN61000-3-2, EN61000-3-3 | MODBUS (remote), USB (local) | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Field_Kit_for_930_Pressure_Monitor_5e0de6e3.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\Field_Kit_for_930_Pressure_Monitor_5e0de6e3.pdf'; verify before quoting.
PROD_PDF_SERVERON_TM8_HELIUM_AND_CALIBRATION_CYLINDERS | Serveron TM8 Helium and Calibration Cylinders | PF_DGA | Online DGA Monitor | TR_DGA_001 | Oil-filled transformer | High-capacity helium carrier gas cylinder and calibration gas cylinder accessories for the Serveron TM8 online multigas DGA monitor. | TPED 2010/35EU, EN ISO 22435, EN ISO 15996, EN ISO 11114-1, EN ISO 10297, EN ISO 837-1 |  | QR_TR_DGA_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Helium_Tank_752be440.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\Helium_Tank_752be440.pdf'; verify before quoting.
PROD_PDF_QUALITROL_505_ITM | Qualitrol 505 ITM | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Intelligent transformer monitor for temperature, cooling control, and dynamic loading analysis of oil-filled transformers and LTCs. | IEEE C37.90.1; IEC 61000-6-1; IEC 61000-6-2; IEC 61010-1; CE approved | DNP 3.0 level 3 slave; Modbus RTU; ASCII | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_505_88332a90.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\ITM_505_88332a90.pdf'; verify before quoting.
PROD_PDF_QUALITROL_507_ITM | Qualitrol 507 ITM | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Intelligent Transformer Monitor with fiber optic direct winding temperature monitoring, cooling control, and TransLife asset life analysis for oil-filled transformers. | IEEE, IEC winding temperature models; ASTM D2413; ASTM D149 | DNP 3.0, Modbus over RS485/RS232 | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_507_1210b08e.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\ITM_507_1210b08e.pdf'; verify before quoting.
PROD_PDF_QUALITROL_506_VTM | Qualitrol 506 VTM | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Vault Transformer Monitor providing remote monitoring of oil-filled transformer pressure, level, temperature and cooling control with fixed or wireless connectivity. | IEEE, IEC winding temperature models | DNP 3.0, Modbus over RS485/RS232 | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_507_1210b08e.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\ITM_507_1210b08e.pdf'; verify before quoting.
PROD_PDF_QUALITROL_509_ITM | QUALITROL 509 ITM | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Intelligent transformer monitor for tracking and controlling oil-filled power transformers and load tap changers, including cooling control, alarming, data logging and TransLife asset-life analysis. | IEEE C37.90.1; IEC 61000-6-1; IEC 61000-6-2; IEC 61010-1; CE approved | DNP 3.0 level 1 slave, Modbus RTU, ASCII, IEC 61850, IEC 60870 | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_509_369c448e.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\ITM_509_369c448e.pdf'; verify before quoting.
PROD_PDF_JBOX2_JB2_SS | JBox2 (JB2-SS) | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | 2nd generation stainless steel junction box protecting fiber optic connections at the tank wall interface of oil-filled power transformers. |  |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/JB2-SS_Junction_Box_8efd0c4c.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\JB2-SS_Junction_Box_8efd0c4c.pdf'; verify before quoting.
PROD_PDF_TWP_TANK_WALL_PLATE | TWP Tank Wall Plate | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Transformer tank wall plate for Neoptix optical feedthroughs (OFT), available in bolt-on and weld-on versions. |  |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/JB2-SS_Junction_Box_8efd0c4c.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\JB2-SS_Junction_Box_8efd0c4c.pdf'; verify before quoting.
PROD_PDF_QUALITROL_LPRD | QUALITROL LPRD | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Large pressure relief device; mechanical device for relief of excessive pressure buildup in transformers, load tap changers and related electrical equipment; auto-reseal dual gasket design. | ASTM B:117; ASTM A229; ISO 9001 |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/LPRD_Large_Pressure_Relief_Devices_72428d97.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\LPRD_Large_Pressure_Relief_Devices_72428d97.pdf'; verify before quoting.
PROD_PDF_NEOPTIX_T1_PROBE | Neoptix T1 Probe | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Fiber optic temperature probe based on GaAs technology for general purpose temperature measurements with immunity to electromagnetic fields. |  |  | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Neoptix_T1_Fiber_Optic_Temperature_Probe_cf61e6a9.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\Neoptix_T1_Fiber_Optic_Temperature_Probe_cf61e6a9.pdf'; verify before quoting.
PROD_PDF_QUALITROL_NEOPTIX_T2_PROBE_T2S | Qualitrol Neoptix T2 Probe (T2S) | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Fiber optic temperature probe for measuring hot spot temperature inside oil-filled or dry-type power transformers and reactors. | ASTM D149; ASTM D2413 |  | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Neoptix_T2_Transformer_Temperature_Probe_7024aafc.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\Neoptix_T2_Transformer_Temperature_Probe_7024aafc.pdf'; verify before quoting.
PROD_PDF_NOMAD_DIRECT | NOMAD-Direct | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Dual-channel portable fiber optic test device for testing fiber optic probe health during transformer manufacturing; immune to EMI and RFI, compatible with Qualitrol Neoptix T1 and T2 probes. | CSA 61010-1, UL61010-1 |  | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/NOMAD-Direct_Fiber-Optic_Temperature_Monitor_d7b954be.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\NOMAD-Direct_Fiber-Optic_Temperature_Monitor_d7b954be.pdf'; verify before quoting.
PROD_PDF_QUALITROL_QHS393 | Qualitrol QHS393 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | High accuracy moisture in oil and temperature sensor measuring water activity, oil temperature and calculated absolute water content; compatible with Serveron DGA monitors and Qualitrol 509/QTMS. | IEC 61326-1; IEC 61326-2-3; IEC 61010-1 | Modbus RTU via RS485; 2 x 4-20mA analog outputs | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Oil_and_Moisture_Temperature_Sensor_acc1b1e0.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\Oil_and_Moisture_Temperature_Sensor_acc1b1e0.pdf'; verify before quoting.
PROD_PDF_QUALITROL_OFT_OFT_1 | QUALITROL OFT (OFT-1) | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Leak-free optical feedthrough providing long-term fiber optic connection through transformer tank walls for oil-filled and dry-type power transformers. | ANSI/ASME B1.20.1 |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Optical_Feedthrough_(OFT)_65c52d3a.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\Optical_Feedthrough_(OFT)_65c52d3a.pdf'; verify before quoting.
PROD_PDF_QUALITROL_KIT_013 | QUALITROL KIT-013 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Complete field test kit for confidence testing of QUALITROL 900/910 Rapid Pressure Rise Relays (RPRRs) while mounted on the transformer. |  |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Rapid_Pressure_Rise_Relay_Test_Kit_7cf61c38.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\Rapid_Pressure_Rise_Relay_Test_Kit_7cf61c38.pdf'; verify before quoting.
PROD_PDF_QUALITROL_STB000_SERIES | Qualitrol STB000 Series | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Universal maintenance-free smart transformer breather that removes moisture from air entering oil-filled transformers or LTC/conservators; auto-regenerates silica gel desiccant via internal heaters. |  | RS-485 Modbus; RJ45 Ethernet; alarm relays; USB local port | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Smart_Transformer_Breathers_b5c5ff49.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\Smart_Transformer_Breathers_b5c5ff49.pdf'; verify before quoting.
PROD_PDF_QUALITROL_OFFSHORE_XTREME_SMART_TRANSFORMER_BREATHER | Qualitrol Offshore Xtreme Smart Transformer Breather | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | NE breather variant engineered with advanced material sets (stainless steel, reinforced fibreglass, glass) to withstand saline offshore environments. |  |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Smart_Transformer_Breathers_b5c5ff49.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\Smart_Transformer_Breathers_b5c5ff49.pdf'; verify before quoting.
PROD_PDF_QUALITROL_POLAR_XTREME_SMART_TRANSFORMER_BREATHER | Qualitrol Polar Xtreme Smart Transformer Breather | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | NE breather variant engineered to house additional heaters preventing condensate freezing at the breather outlet in extremely cold temperatures. |  |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Smart_Transformer_Breathers_b5c5ff49.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\Smart_Transformer_Breathers_b5c5ff49.pdf'; verify before quoting.
PROD_PDF_T_GUARD_LINK_REVB | T/Guard-Link RevB | PF_TR_TEMP | Transformer Temperature Monitor | TR_TEMP_001; DRY_TR_TEMP_001 | Transformer | Fiber optic power transformer winding hot-spot temperature monitoring system for dry-type and oil-filled transformers, linking Neoptix probes to Qualitrol 507/509 controllers. | IEC 61000-4-2/-3/-4/-5/-6; ICES-003; IEC 60255-5; IEEE C37.90; IEEE C37.90.1-2002; IEC 60068-2-14; MIL-I-46058C | RS-485 (Modbus RTU and ASCII); 4-20 mA analog outputs | QR_TR_TEMP_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TGuard_Link_RevB_Fiber-Optic_Hot-Spot_Monitor_b37a6673.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\TGuard_Link_RevB_Fiber-Optic_Hot-Spot_Monitor_b37a6673.pdf'; verify before quoting.
PROD_PDF_QUALITROL_XPRD | Qualitrol XPRD | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Mechanical overpressure protection relief device with integrated directional discharge outlet for transformers and load tap changers; automatically reseals once pressure falls. | IEC; CE; ASTM A229; ASTM B117-90 |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/XPRD_Extra_Large_Pressure_Relief_Device_cf600595.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\XPRD_Extra_Large_Pressure_Relief_Device_cf600595.pdf'; verify before quoting.
PROD_PDF_IDM_PMU_9 | IDM+PMU 9 | PF_PMU | Phasor Measurement Unit | PMU_001 | Grid measurement point | Scalable modular substation-hardened PMU; configurable to monitor one or two circuits with 9 analog and 32 digital channels | IEEE C37.118; IEEE, EU and IEC | IEEE C37.118 phasor streaming; Ethernet (RJ45/fibre) | QR_PMU_001 |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'The_Power_Grid\IDM+PMU_7cb7c557.pdf'; verify before quoting.
PROD_PDF_IDM_PMU_18 | IDM+PMU 18 | PF_PMU | Phasor Measurement Unit | PMU_001 | Grid measurement point | Scalable modular substation-hardened PMU configurable to monitor three or five circuits with 18 analog and 32 digital channels | IEEE C37.118; IEEE, EU and IEC | IEEE C37.118 phasor streaming; Ethernet (RJ45/fibre) | QR_PMU_001 |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'The_Power_Grid\IDM+PMU_7cb7c557.pdf'; verify before quoting.
PROD_PDF_IDM_PMU_36 | IDM+PMU 36 | PF_PMU | Phasor Measurement Unit | PMU_001 | Grid measurement point | Scalable modular substation-hardened PMU configurable to monitor six or ten circuits with 36 analog and 64 digital channels; connection to up to ten three-phase circuits | IEEE C37.118; IEEE, EU and IEC | IEEE C37.118 phasor streaming; Ethernet (RJ45/fibre) | QR_PMU_001 |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'The_Power_Grid\IDM+PMU_7cb7c557.pdf'; verify before quoting.
PROD_PDF_QUALITROL_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATOR | Qualitrol AKM 44712/34725 Large Oil Level Indicator | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Large oil level indicators with M50 thread mount; gear (34725) or lever (44712) driven float mechanisms; up to 4 integrated switches for level alarm control. |  | 4-20mA analog output | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/045_Liquid_Level_Gauge_09f522e9.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\045_Liquid_Level_Gauge_09f522e9.pdf'; verify before quoting.
PROD_PDF_AKM_35600_47500 | AKM 35600 / 47500 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Rugged weatherproof pressure or vacuum switch with fast snap-action reaction for transformers and LTCs. | UL, CSA listed |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_47500_Pressure_Control_Switches_1068660c.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\AKM_47500_Pressure_Control_Switches_1068660c.pdf'; verify before quoting.
PROD_PDF_QUALITROL_AKM_47500 | QUALITROL AKM 47500 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | TR_AUX_001; CAB_ENV_001 | Transformer / cabinet | Pressure or vacuum switch (specifications shared with 35600 series). | UL, CSA |  | QR_TR_AUX_001 |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/148_PressureVacuum_Switch_2a33e83a.pdf | Datasheet PDF (Step 0b) | Candidate | Datasheet-sourced (Step 0b) from 'Transformer_Monitoring\148_PressureVacuum_Switch_2a33e83a.pdf'; verify before quoting.
PROD_PF_DAU_REC_01 | IDM+ 27A/64D | PF_DAU_REC | Multi-function DAU / Recorder (IDM+ / Informa) | FMS_001;DFR_DDR_001;PMU_001;WAMS_001;PQ_CLASSA_001 | Bay / Feeder | Multi-function disturbance / fault / PQ / phasor recorder DAU, 27 analogue / 64 digital channels; one per HV bay (CPU can be time master). |  |  | QR_DAU_BAY_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_DAU_REC_02 | IDM+ 18A/32D | PF_DAU_REC | Multi-function DAU / Recorder (IDM+ / Informa) | FMS_001;DFR_DDR_001 | Bay / Feeder | FMS/DFR data-acquisition unit, 18 analogue / 32 digital channels. |  |  | QR_DAU_BAY_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_DAU_REC_03 | IDM+ 9A/32D | PF_DAU_REC | Multi-function DAU / Recorder (IDM+ / Informa) | FMS_001;PMU_001;WAMS_001 | Bay / Feeder | Compact DAU, 9 analogue / 32 digital channels; used on 132/11kV bays and for PMU. |  |  | QR_DAU_BAY_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_DAU_REC_04 | Informa 9A/32D | PF_DAU_REC | Multi-function DAU / Recorder (IDM+ / Informa) | PQ_CLASSA_001 | Bay / Feeder | Power-quality DAU (Class A), 9 analogue / 32 digital channels; one per PQ-monitored bay. |  |  | QR_DAU_BAY_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_SW_LIC_05 | EPG PMU license | PF_SW_LIC | Monitoring Software & Licences | PMU_001 | System | EPG phasor measurement (PMU) software licence, allocated per PMU channel/bay. |  |  | QR_PER_SYSTEM_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_SW_LIC_06 | EPG WAMS Software License | PF_SW_LIC | Monitoring Software & Licences | WAMS_001 | System | EPG wide-area monitoring (WAMS) software licence. |  |  | QR_PER_SYSTEM_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_SW_LIC_07 | iQ+ (5 users, 25 devices) | PF_SW_LIC | Monitoring Software & Licences | COMM_SCADA_001 | System | iQ+ master-station / fault-location software; quoted once per system (user/device tiers). |  |  | QR_PER_SYSTEM_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_SW_LIC_08 | Trend Micro Antivirus (3yr) | PF_SW_LIC | Monitoring Software & Licences | COMM_SCADA_001 | System | Endpoint antivirus for the monitoring PCs (Transco cybersecurity). |  |  | QR_PER_SYSTEM_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_SW_LIC_09 | Trellix Whitelisting Software (3yr) | PF_SW_LIC | Monitoring Software & Licences | COMM_SCADA_001 | System | Application whitelisting for the monitoring PCs. |  |  | QR_PER_SYSTEM_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_SW_LIC_10 | Acronis Backup | PF_SW_LIC | Monitoring Software & Licences | COMM_SCADA_001 | System | Backup software for the monitoring PCs. |  |  | QR_PER_SYSTEM_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_MON_PANEL_11 | Industrial Rack Mounted PC | PF_MON_PANEL | Monitoring Panel / Cabinet | COMM_SCADA_001 | Panel | Industrial rack-mounted PC for FMS/PQM/PDC/PMU station (plus backup PC). |  |  | QR_PER_SYSTEM_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_MON_PANEL_12 | Monitor, Keyboard | PF_MON_PANEL | Monitoring Panel / Cabinet | COMM_SCADA_001 | Panel | Operator monitor and keyboard for the LEV/PDC cabinet. |  |  | QR_PER_SYSTEM_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_MON_PANEL_13 | KVM | PF_MON_PANEL | Monitoring Panel / Cabinet | COMM_SCADA_001 | Panel | KVM switch for the PDC cabinet. |  |  | QR_PER_SYSTEM_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_MON_PANEL_14 | Printer | PF_MON_PANEL | Monitoring Panel / Cabinet | COMM_SCADA_001 | Panel | Report printer for the LEV cabinet. |  |  | QR_PER_SYSTEM_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_MON_PANEL_15 | Alarm Annunciator | PF_MON_PANEL | Monitoring Panel / Cabinet | COMM_SCADA_001 | Panel | Alarm annunciator for the monitoring panel. |  |  | QR_PER_SYSTEM_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_NET_SEC_16 | 16 Port RJ45 + fiber L2 switch | PF_NET_SEC | Network & Security Equipment | COMM_SCADA_001 | Panel | Managed layer-2 Ethernet switch (RJ45 + fiber uplinks) for the monitoring LAN; port/fiber count varies (4/8/16). |  |  | QR_PER_PANEL_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_NET_SEC_17 | 16 Port RJ45 + fiber L3 switch | PF_NET_SEC | Network & Security Equipment | COMM_SCADA_001 | Panel | Managed layer-3 Ethernet switch (RJ45 + fiber) for routing to LDC/TCC. |  |  | QR_PER_PANEL_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_NET_SEC_18 | Firewall | PF_NET_SEC | Network & Security Equipment | COMM_SCADA_001 | Panel | Firewall for the monitoring LAN / OETC connection (optional per architecture). |  |  | QR_PER_PANEL_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_TIMING_19 | GPS Antenna & Cable (100m) + amplifier + mounting kit + surge arrestor | PF_TIMING | GPS Timing | PMU_001;WAMS_001 | System | GPS timing antenna kit for time-synchronised PMU/WAMS. |  |  | QR_PER_SYSTEM_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_TIMING_20 | 2-Way GPS Splitter | PF_TIMING | GPS Timing | PMU_001;WAMS_001 | System | GPS signal splitter feeding multiple DAUs from one antenna. |  |  | QR_PER_SYSTEM_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_PANEL_ACC_21 | Test Switches | PF_PANEL_ACC | Panel Accessories | FMS_001;PMU_001;PQ_CLASSA_001 | Bay | Test/isolation switches per DAU/bay. |  |  | QR_PER_DAU_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_MON_PANEL_22 | FMS Panel (as per Transco Spec) | PF_MON_PANEL | Monitoring Panel / Cabinet | FMS_001 | Panel | FMS field panel housing the FMS DAUs and accessories. |  |  | QR_PANEL_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_MON_PANEL_23 | WAMS/PQM Panel (as per Transco Spec) | PF_MON_PANEL | Monitoring Panel / Cabinet | PMU_001;WAMS_001;PQ_CLASSA_001 | Panel | WAMS/PQM field panel housing the PMU/PQ DAUs and accessories. |  |  | QR_PANEL_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_MON_PANEL_24 | LEV Cubicle (as per Transco Spec) | PF_MON_PANEL | Monitoring Panel / Cabinet | COMM_SCADA_001 | Panel | Local equipment (LEV) cubicle housing the station PC, network and software. |  |  | QR_PANEL_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_MON_PANEL_25 | PDC Cubicle (as per Transco Spec) | PF_MON_PANEL | Monitoring Panel / Cabinet | PMU_001;WAMS_001 | Panel | PDC cubicle housing the PDC/PMU servers, network and software. |  |  | QR_PANEL_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_SERVICES_26 | Factory FAT | PF_SERVICES | Engineering & Commissioning Services | COMM_SCADA_001 | System | Factory acceptance testing of the panels (day-rate; typ. 2–5 days). |  |  | QR_SERVICES_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_SERVICES_27 | Testing & Commissioning | PF_SERVICES | Engineering & Commissioning Services | COMM_SCADA_001 | System | Site testing & commissioning (day-rate; scales with panel/bay count). |  |  | QR_SERVICES_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_SERVICES_28 | Communication Establishment (LDC/TCC/REV-E4) | PF_SERVICES | Engineering & Commissioning Services | COMM_SCADA_001 | System | Communication link establishment with LDC/TCC/REV/E4 (day-rate). |  |  | QR_SERVICES_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_SERVICES_29 | Cybersecurity Service | PF_SERVICES | Engineering & Commissioning Services | COMM_SCADA_001 | System | Cybersecurity hardening/config (day-rate). |  |  | QR_SERVICES_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_SERVICES_30 | Energisation Assistance | PF_SERVICES | Engineering & Commissioning Services | COMM_SCADA_001 | System | Energisation support (day-rate + mobilisation). |  |  | QR_SERVICES_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_SERVICES_31 | Training | PF_SERVICES | Engineering & Commissioning Services | COMM_SCADA_001 | System | Operator/maintenance training (TBA). |  |  | QR_SERVICES_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_PF_SERVICES_32 | Mandatory Spares 10% | PF_SERVICES | Engineering & Commissioning Services | COMM_SCADA_001 | System | Mandatory spare parts, typically 10% of hardware. |  |  | QR_SERVICES_001 |  |  |  | BOQ reverse-extraction | candidate | Auto-added from BOQ reverse-extraction (775368 / 776060 / MEA Example BOQ); candidate — review before use.
PROD_MEA_PF_DAU_REC_01 | IDM+ 18A/64D | PF_DAU_REC | Multi-function DAU / Recorder (IDM+ / Informa) | FMS_001;PQ_CLASSA_001 | Bay / Feeder | 6U DAU chassis, 18 analogue / 64 digital channels; TAQA-approved for FMS/PQM (and FMS/PMU). |  |  | QR_DAU_BAY_001 |  |  |  | TAQA MEA ruleset | candidate | TAQA/ADNOC MEA ruleset (Ruleset for TAQA ADNOC MEA Region - IP.xlsx); candidate — review before use.
PROD_MEA_PF_DAU_REC_02 | IDM+ 27A/96D | PF_DAU_REC | Multi-function DAU / Recorder (IDM+ / Informa) | PQ_CLASSA_001 | Bay / Feeder | 6U DAU chassis, 27 analogue / 96 digital channels; TAQA-approved for PQM. |  |  | QR_DAU_BAY_001 |  |  |  | TAQA MEA ruleset | candidate | TAQA/ADNOC MEA ruleset (Ruleset for TAQA ADNOC MEA Region - IP.xlsx); candidate — review before use.
PROD_MEA_PF_DAU_REC_03 | IDM+ 36A/128D | PF_DAU_REC | Multi-function DAU / Recorder (IDM+ / Informa) | PMU_001 | Bay / Feeder | 6U DAU chassis, 36 analogue / 128 digital channels; TAQA-approved for PMU on OHL/IC/Gen feeders. |  |  | QR_DAU_BAY_001 |  |  |  | TAQA MEA ruleset | candidate | TAQA/ADNOC MEA ruleset (Ruleset for TAQA ADNOC MEA Region - IP.xlsx); candidate — review before use.
PROD_MEA_PF_SW_LIC_04 | eSPDC Software | PF_SW_LIC | Monitoring Software & Licences | PMU_001;WAMS_001 | System | eSPDC phasor data concentrator software for the PDC panel. |  |  | QR_PER_SYSTEM_001 |  |  |  | TAQA MEA ruleset | candidate | TAQA/ADNOC MEA ruleset (Ruleset for TAQA ADNOC MEA Region - IP.xlsx); candidate — review before use.

## 08_Product_Parameter_Template
Product Parameter Template - One Row Per Product Parameter
Avoid wide columns such as Parameter 1/2/3. Use this normalized table for matching.
Product ID | Product Model | Product Family ID | Parameter ID | Parameter Name | Min Value | Max Value | Supported Value / Text | Unit | Match Type | Match Priority | Evidence Source / Datasheet URL | Notes
| Reference; matching keys on Parameter ID only. | Reference; matching keys on Parameter ID only. | Metric ID (sheet 04) this product covers; THE field used for must-have coverage. | Reference/display; not used in matching. | Lower bound; loaded but range-matching not yet implemented. | Upper bound; loaded but range-matching not yet implemented. | Supported spec value; loaded but value-matching not yet implemented. | Reference; not used in matching. | Planned (exact/range/contains); not yet used by the pipeline. | Planned priority; not yet used by the pipeline. | Source link; NOT read by the pipeline. | Human note; not used by matching.
PROD_PF_PD_TRANSFORMER_01 | QPDM | PF_PD_TRANSFORMER | MET_ASSET_TYPE | Asset Type |  |  | Power transformer | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PD_TRANSFORMER_01 | QPDM | PF_PD_TRANSFORMER | MET_SENSOR_TYPE | Sensor Type |  |  | UHF | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PD_TRANSFORMER_01 | QPDM | PF_PD_TRANSFORMER | MET_PD_LEVEL | Built-in Sensitivity |  | -80 | -80 dBm sensitivity, 70 dB dynamic range, 300-2100 MHz band | dBm |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PD_TRANSFORMER_01 | QPDM | PF_PD_TRANSFORMER | MET_ENCLOSURE_RATING | Enclosure Rating |  |  | IP66 | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PD_TRANSFORMER_02 | QPPDM | PF_PD_TRANSFORMER | MET_ASSET_TYPE | Asset Type |  |  | Power transformer / GIS | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PD_TRANSFORMER_02 | QPPDM | PF_PD_TRANSFORMER | MET_SENSOR_TYPE | Sensor Type |  |  | UHF PD | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_01 | QBCM | PF_BREAKER | MET_ASSET_TYPE | Asset Type |  |  | Circuit breaker | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_01 | QBCM | PF_BREAKER | MET_COIL_CURRENT | Coil Current Signature |  |  | Coil current signature monitoring | A |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_01 | QBCM | PF_BREAKER | MET_TRIP_CLOSE_TIME | Travel Curve / Operating Time |  |  | Travel curves and operating mechanism timing | ms |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_01 | QBCM | PF_BREAKER | MET_SF6_PRESSURE | SF6 Density Trend |  |  | SF6 density trend monitoring | density |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_01 | QBCM | PF_BREAKER | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850, COMTRADE | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_02 | QBCM Software | PF_BREAKER | MET_ASSET_TYPE | Asset Type |  |  | Circuit breaker | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_02 | QBCM Software | PF_BREAKER | MET_LICENSE_SCOPE | Software License Scope |  |  | Diagnostics and analytics software for breaker fleet | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_03 | HATHAWAY CBT 200/400 | PF_BREAKER | MET_ASSET_TYPE | Asset Type |  |  | Circuit breaker | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_BREAKER_04 | HATHAWAY BCM 200/200E | PF_BREAKER | MET_ASSET_TYPE | Asset Type |  |  | Circuit breaker | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_01 | Gen 3 PDM | PF_GIS_PD | MET_SENSOR_TYPE | Sensor Type |  |  | UHF sensors | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_01 | Gen 3 PDM | PF_GIS_PD | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850 | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_01 | Gen 3 PDM | PF_GIS_PD | MET_ASSET_TYPE | Asset Type |  |  | GIS | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_02 | PDMG-RH - Gen 3 | PF_GIS_PD | MET_SENSOR_TYPE | Sensor Type |  |  | UHF | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_02 | PDMG-RH - Gen 3 | PF_GIS_PD | MET_ASSET_TYPE | Asset Type |  |  | GIS | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_03 | Portable PDM | PF_GIS_PD | MET_SENSOR_TYPE | Sensor Type |  |  | UHF, Wideband 300-1500 MHz | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_03 | Portable PDM | PF_GIS_PD | MET_SENSOR_COUNT | UHF Channels |  |  | 6 UHF channels + 1 noise antenna channel | count |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_03 | Portable PDM | PF_GIS_PD | MET_PD_LEVEL | PD Sensitivity |  |  | < 5 pC | pC |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_03 | Portable PDM | PF_GIS_PD | MET_SAMPLING_RATE | Sampling Rate |  |  | 15.4 KS/s per channel; total 107.5 KS/s for 7 channels (also 51000 samples per second cited) | samples/s |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_03 | Portable PDM | PF_GIS_PD | MET_POWER_SUPPLY | Power Supply |  |  | 90 to 264 VAC, 47-63 Hz; 40 to 290 VDC universal supply | V AC/DC |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_03 | Portable PDM | PF_GIS_PD | MET_NETWORK | Network Interface |  |  | RJ45 (10/100 Mbps), USB | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_03 | Portable PDM | PF_GIS_PD | MET_ALARM_THRESHOLD | Alarm Indications |  |  | PD fault alarm, PD alarm, PD warning alarm, system status | varies |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_04 | QPDM | PF_GIS_PD | MET_SENSOR_TYPE | Sensor Type |  |  | UHF | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_04 | QPDM | PF_GIS_PD | MET_PD_LEVEL | Dynamic Range |  |  | 70 dB | dB |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GIS_PD_04 | QPDM | PF_GIS_PD | MET_ENCLOSURE_RATING | Enclosure Rating |  |  | IP66 | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_SENSOR_TYPE | Sensor Type |  |  | UHF | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_SENSOR_COUNT | UHF Sensor Inputs | 1 | 24 | 1–6 channels, expandable to 24 | count |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_PD_LEVEL | Dynamic Range / Sensitivity |  |  | 70 dB dynamic range; sensitivity -75 to -80 dBm | dB |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_SAMPLING_RATE | Sampling Rate |  |  | 15,360 samples/s @ 60 Hz | samples/s |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_ENCLOSURE_RATING | Environmental Rating |  |  | IP66 | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_AMBIENT_TEMP | Operating Temperature Range | -25 | 55 | -25°C to +55°C | °C |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_HUMIDITY | Humidity | 5 | 95 | 5–95% | %RH |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850, Modbus | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_01 | QPDM | PF_SWG_PD | MET_NETWORK | Network Interface |  |  | Ethernet (RJ45/fiber) | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_02 | QPPDM | PF_SWG_PD | MET_SENSOR_TYPE | Sensor Type |  |  | UHF | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_03 | PDMG-RH Gen 3 | PF_SWG_PD | MET_SENSOR_TYPE | Sensor Type |  |  | UHF | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SWG_PD_04 | IC44 | PF_SWG_PD | MET_SENSOR_TYPE | Sensor Type |  |  | UHF coupler | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_PD_01 | PDTracII 4208 | PF_GEN_PD | MET_SENSOR_TYPE | Sensor Type |  |  | Iris Power Epoxy Mica Capacitor Couplers | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_PD_01 | PDTracII 4208 | PF_GEN_PD | MET_PD_LEVEL | Partial Discharge Monitoring |  |  | Continuous online PD measurement | pC / mV / dB |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_PD_01 | PDTracII 4208 | PF_GEN_PD | MET_ASSET_TYPE | Asset Type |  |  | Generator/Motor | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_EWV_01 | EVAII | PF_GEN_EWV | MET_SENSOR_TYPE | Sensor Type |  |  | Fiber optic accelerometer (all dielectric, no metallic parts) | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_EWV_01 | EVAII | PF_GEN_EWV | MET_VIBRATION | Vibration Dynamic Range | 0 | 50 | 0-50 g, resolution <0.007 g | g |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_EWV_01 | EVAII | PF_GEN_EWV | MET_AMBIENT_TEMP | Operating Temperature Range | -50 | 200 | -50°C to +200°C | °C |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_EWV_03 | EVTracII | PF_GEN_EWV | MET_ASSET_TYPE | Asset Type |  |  | Generator | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_03 | Iris Power Capacitive Air Gap Sensor (CGS) | PF_GEN_AIRGAP | MET_SENSOR_TYPE | Sensor Type |  |  | Capacitive gap probe with linearization module | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_03 | Iris Power Capacitive Air Gap Sensor (CGS) | PF_GEN_AIRGAP | MET_AIR_GAP | Air Gap |  |  | Output directly proportional to air gap distance (pole profile) | mm / % |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_03 | Iris Power Capacitive Air Gap Sensor (CGS) | PF_GEN_AIRGAP | MET_ENCLOSURE_RATING | Case Protection Class |  |  | IP66 | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_03 | Iris Power Capacitive Air Gap Sensor (CGS) | PF_GEN_AIRGAP | MET_ASSET_TYPE | Asset Type |  |  | Hydro generator | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_04 | Iris Power TGA-S | PF_GEN_AIRGAP | MET_PD_LEVEL | Partial Discharge Level |  |  | Stator winding partial discharge monitoring | pC / mV / dB |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_04 | Iris Power TGA-S | PF_GEN_AIRGAP | MET_ASSET_TYPE | Asset Type |  |  | Generator | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_05 | Iris Power GuardII+ | PF_GEN_AIRGAP | MET_PD_LEVEL | Partial Discharge Level |  |  | Online partial discharge monitoring | pC / mV / dB |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GEN_AIRGAP_05 | Iris Power GuardII+ | PF_GEN_AIRGAP | MET_ASSET_TYPE | Asset Type |  |  | Generator | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_MOTOR_01 | PDTracII 4208 | PF_MOTOR | MET_ASSET_TYPE | Asset Type |  |  | Large motor | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_MOTOR_01 | PDTracII 4208 | PF_MOTOR | MET_SENSOR_TYPE | PD Coupler Type |  |  | Iris Power Epoxy Mica Capacitor Couplers | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_MOTOR_01 | PDTracII 4208 | PF_MOTOR | MET_PD_LEVEL | Partial Discharge Measurement |  |  | Continuous PD measurement | pC / mV / dB |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_MOTOR_02 | PPM-97 Corona Probe | PF_MOTOR | MET_ASSET_TYPE | Asset Type |  |  | Motors & Generators | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_MOTOR_02 | PPM-97 Corona Probe | PF_MOTOR | MET_PD_LEVEL | Partial Discharge Detection |  |  | Offline PD location | pC / mV / dB |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_01 | BEN 6000 | PF_PQ | MET_PQ_CLASS | Power Quality Class |  |  | Class A (IEC 61000-4-30) | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_01 | BEN 6000 | PF_PQ | MET_SAG_SWELL | Sag / Swell Recording |  |  | PQ event detection, capture and trends | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_01 | BEN 6000 | PF_PQ | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850 GOOSE | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_01 | BEN 6000 | PF_PQ | MET_NETWORK | Network Interface |  |  | Ethernet/LAN | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_02 | BEN 6000 PORTABLE | PF_PQ | MET_PQ_CLASS | Power Quality Class |  |  | Class A | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_02 | BEN 6000 PORTABLE | PF_PQ | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850 GOOSE | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_03 | BEN 600 | PF_PQ | MET_PQ_CLASS | Power Quality Class |  |  | Class A | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_03 | BEN 600 | PF_PQ | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850 GOOSE | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PQ_04 | IDM | PF_PQ | MET_PQ_CLASS | Power Quality Class |  |  | Class A (optional) | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_01 | HATHAWAY IDM | PF_PMU | MET_CURRENT_CHANNELS | Analog channels (max) |  | 192 | Up to 192 analog channels | count |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_01 | HATHAWAY IDM | PF_PMU | MET_PQ_CLASS | Power Quality Class |  |  | Class A | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_01 | HATHAWAY IDM | PF_PMU | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850 Goose messaging | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_02 | HATHAWAY IDM PORTABLE | PF_PMU | MET_CURRENT_CHANNELS | Analog channels (max) |  | 192 | Up to 192 analog channels | count |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_02 | HATHAWAY IDM PORTABLE | PF_PMU | MET_PQ_CLASS | Power Quality Class |  |  | Class A | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_02 | HATHAWAY IDM PORTABLE | PF_PMU | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850 Goose messaging | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_03 | BEN 6000 PORTABLE | PF_PMU | MET_CURRENT_CHANNELS | Analog channels |  | 16 | 16 analog channels, expandable via remote acquisition units | count |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_03 | BEN 6000 PORTABLE | PF_PMU | MET_PQ_CLASS | Power Quality Class |  |  | Class A | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_PMU_03 | BEN 6000 PORTABLE | PF_PMU | MET_PROTOCOL | Communication Protocol |  |  | IEC 61850 Goose messaging | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_01 | ITM Remote | PF_SOFTWARE | MET_ASSET_TYPE | Asset Type |  |  | Transformer | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_01 | ITM Remote | PF_SOFTWARE | MET_LICENSE_SCOPE | Software License Scope |  |  | Transformer fleet life management software | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_02 | SmartSub | PF_SOFTWARE | MET_ASSET_TYPE | Asset Type |  |  | Substation / multi-asset | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_02 | SmartSub | PF_SOFTWARE | MET_LICENSE_SCOPE | Software License Scope |  |  | Substation asset performance management | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_04 | TMView | PF_SOFTWARE | MET_ASSET_TYPE | Asset Type |  |  | Transformer | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_05 | QTMS | PF_SOFTWARE | MET_ASSET_TYPE | Asset Type |  |  | Transformer | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_05 | QTMS | PF_SOFTWARE | MET_PROTOCOL | Communication Protocol |  |  | DNP 3.0 (Level3), Modbus, IEC 60870-104-5, IEC 61850 | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_05 | QTMS | PF_SOFTWARE | MET_NETWORK | Network Interface |  |  | Serial; Ethernet | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_SOFTWARE_05 | QTMS | PF_SOFTWARE | MET_REPORTING_RATE | Data Logging / Store Rate |  |  | 100 variables; store rates 1 minute to 24 hours; 32 parameters at 15 second capture rate for 90 days (4 GB memory) | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GATEWAY_01 | QGateway (GTW-SP-EP) | PF_GATEWAY | MET_ASSET_TYPE | Asset Type |  |  | Monitoring system / protocol gateway | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GATEWAY_01 | QGateway (GTW-SP-EP) | PF_GATEWAY | MET_PROTOCOL | Communication Protocols |  |  | Modbus, DNP 3.0, IEC 61850, IEC 60870-5-104, HTTP | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GATEWAY_01 | QGateway (GTW-SP-EP) | PF_GATEWAY | MET_NETWORK | Network Interface |  |  | 2 x RS-485 Full-Duplex serial inputs; 1 x isolated RJ-45 Ethernet port | text |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GATEWAY_01 | QGateway (GTW-SP-EP) | PF_GATEWAY | MET_POWER_SUPPLY | Power Requirements |  |  | 24 VDC | V DC |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_GATEWAY_01 | QGateway (GTW-SP-EP) | PF_GATEWAY | MET_AMBIENT_TEMP | Operating Temperature |  |  | Operating/storage temperature range (per datasheet) | °C |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_DFR_02 | iQ+ | PF_DFR | MET_LICENSE_SCOPE | Master Station Software |  |  | Master station software scope | text |  |  |  | Tavily-sourced; verify against datasheet.
PROD_PF_TWS_01 | HATHAWAY MARK VI | PF_TWS | MET_ASSET_COUNT | Lines Monitored per Device |  | 8 | Up to 8 lines | count |  |  | https://offers.qualitrolcorp.com/hubfs/CA-X00-00A-02E_Product_Overview_Catalog.pdf
PROD_PF_TWS_01 | HATHAWAY MARK VI | PF_TWS | MET_COMM_PROTOCOL | Communication Protocol |  |  | DNP 3.0; Modem; Ethernet
PROD_PF_TWS_03 | IDM+ (TWS function) | PF_TWS | MET_TIME_SYNC | Time Synchronization |  |  | GPS; 100 ns time tagging precision
PROD_PF_DFR_03 | Analog Channels | 9 | count | integer | 3U, single analog card block
PROD_PF_DFR_03 | Digital Channels | 32 | count | integer | 32 digital inputs standard
PROD_PF_DFR_03 | Form Factor | 3U (133 mm H × 483 mm W) | text | text | 19-inch rack mountable
PROD_PF_DFR_03 | DFR Sampling Rate | 512 samples/cycle (30.7 kHz@60Hz; 25.6 kHz@50Hz) | Hz | text | Selectable: 512/256/128/64/32 s/c
PROD_PF_DFR_03 | Analog Resolution | 20-bit current; 16-bit voltage/DC | bits | text
PROD_PF_DFR_03 | Accuracy | ±0.1% full scale | % | text
PROD_PF_DFR_03 | Data Storage | 4 GB CompactFlash standard; opt 8/16 GB | GB | text
PROD_PF_DFR_03 | Time Synchronization | GPS (100 ns); IRIG-B/J; 1 pps | ns | text
PROD_PF_DFR_03 | Operating Temperature | -5 to +50°C operating; -30 to +70°C storage | °C | text
PROD_PF_DFR_03 | Communication Protocol | IEC 61850; IEC 60870-5-104; DNP 3.0; Modbus | text | text
PROD_PF_DFR_03 | Optional Functions | PMU (IEEE C37.118-2014); TWS card (±60m FL); Class A PQ | text | text | Each option ordered separately
PROD_PF_DFR_03 | Asset Type | Substation bus / feeder / plant bus | text | text
PROD_PF_DFR_04 | Analog Channels | 18 | count | integer | 6U, two 9-channel analog blocks
PROD_PF_DFR_04 | Digital Channels | 64 | count | integer | 64 digital inputs standard
PROD_PF_DFR_04 | Form Factor | 6U (267 mm H × 483 mm W) | text | text | 19-inch rack mountable
PROD_PF_DFR_04 | DFR Sampling Rate | 512 samples/cycle (30.7 kHz@60Hz; 25.6 kHz@50Hz) | Hz | text
PROD_PF_DFR_04 | Data Storage | 4 GB CompactFlash standard; opt 8/16 GB | GB | text
PROD_PF_DFR_04 | Time Synchronization | GPS (100 ns); IRIG-B/J; 1 pps | ns | text
PROD_PF_DFR_04 | Communication Protocol | IEC 61850; IEC 60870-5-104; DNP 3.0; Modbus | text | text
PROD_PF_DFR_04 | Optional Functions | PMU (IEEE C37.118-2014); TWS card (±60m FL); Class A PQ | text | text
PROD_PF_DFR_04 | Operating Temperature | -5 to +50°C operating | °C | text
PROD_PF_DFR_04 | Asset Type | Substation bus / feeder / plant bus | text | text
PROD_PF_DFR_05 | Analog Channels | 36 | count | integer | 6U, four 9-channel analog blocks
PROD_PF_DFR_05 | Digital Channels | 128 | count | integer | 128 digital inputs standard
PROD_PF_DFR_05 | Form Factor | 6U (267 mm H × 483 mm W) | text | text | 19-inch rack mountable
PROD_PF_DFR_05 | DFR Sampling Rate | 512 samples/cycle (30.7 kHz@60Hz; 25.6 kHz@50Hz) | Hz | text
PROD_PF_DFR_05 | Data Storage | 4 GB standard; opt 8/16 GB | GB | text
PROD_PF_DFR_05 | Time Synchronization | GPS (100 ns); IRIG-B/J; 1 pps | ns | text
PROD_PF_DFR_05 | Communication Protocol | IEC 61850; IEC 60870-5-104; DNP 3.0; Modbus | text | text
PROD_PF_DFR_05 | Optional Functions | PMU (IEEE C37.118-2014); TWS card (±60m FL); Class A PQ | text | text
PROD_PF_DFR_05 | Operating Temperature | -5 to +50°C operating | °C | text
PROD_PF_DFR_05 | Asset Type | Substation bus / feeder / plant bus | text | text
PROD_PF_PMU_04 | Analog channels (max) | 9 / 18 / 36 (per IDM+ variant) | count | text
PROD_PF_PMU_04 | PMU Standard | IEEE C37.118-2014 | text | text
PROD_PF_PMU_04 | PMU Reporting Rate | 25 or 50 fps at 50 Hz; 30 or 60 fps at 60 Hz (typical) | fps | text
PROD_PF_PMU_04 | Time Synchronization | GPS (100 ns) | ns | text
PROD_PF_PMU_04 | Communication Protocol | IEEE C37.118 streaming; IEC 61850 GOOSE; DNP 3.0 | text | text
PROD_PF_PMU_04 | Optional Add-ons | TWS card (fault location); Class A PQ | text | text
PROD_PF_PMU_04 | Asset Type | Transmission grid measurement point / substation bus | text | text
PROD_PDF_ISGM | iSGM | PF_AUX_SENSOR | MET_SENSOR_TYPE | SF6 gas density transducer |  |  | Wika transducers with 4-20 mA outputs | mA |  |  | Preparation/Qualitrol Product/Breakers/iSGM_dde77d65.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: transducers with 4 - 20 mA outputs to capture the SF6 gas density
PROD_PDF_ISGM | iSGM | PF_AUX_SENSOR | MET_SENSOR_COUNT | Maximum tanks monitored | 1 | 2048 | one gas tank to 2048 tanks | count |  |  | Preparation/Qualitrol Product/Breakers/iSGM_dde77d65.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: monitor from as little as one gas tank to 2048 tanks
PROD_PDF_ISGM | iSGM | PF_AUX_SENSOR | MET_NETWORK | Network interface |  |  | Ethernet or Wi-Fi | text |  |  | Preparation/Qualitrol Product/Breakers/iSGM_dde77d65.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Ethernet or Wi-Fi communications
PROD_PDF_ISGM | iSGM | PF_AUX_SENSOR | MET_PROTOCOL | Communication protocols |  |  | DNP 3.0 and IEC 61850 | text |  |  | Preparation/Qualitrol Product/Breakers/iSGM_dde77d65.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Full range of protocols - including DNP 3.0 and IEC 61850
PROD_PDF_ISGM | iSGM | PF_AUX_SENSOR | MET_ALARM_THRESHOLD | Smart Boolean alarms |  |  | Smart (Boolean) alarms on combination of conditions | text |  |  | Preparation/Qualitrol Product/Breakers/iSGM_dde77d65.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Smart (Boolean) alarms to allow alarming on combination of conditions
PROD_PDF_ISGM | iSGM | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Mounting |  |  | DIN rail mounted acquisition node | text |  |  | Preparation/Qualitrol Product/Breakers/iSGM_dde77d65.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: DIN rail mounted acquisition node - for ease of mounting
PROD_PDF_QBCM_QUALITROL_BREAKER_CONDITION_MONITORING | QBCM (Qualitrol Breaker Condition Monitoring) | PF_BREAKER | MET_SAMPLING_RATE | Recording resolution | 32 | 128 | 32 / 64 / 128 samples per cycle | samples/cycle |  |  | Preparation/Qualitrol Product/Breakers/QBCM_9a27f030.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: User selectable for 32 / 64 / 128 samples per cycle
PROD_PDF_QBCM_QUALITROL_BREAKER_CONDITION_MONITORING | QBCM (Qualitrol Breaker Condition Monitoring) | PF_BREAKER | MET_DFR_FUNCTIONS | Operation storage capacity |  | 10000 | up to 10,000 operations records | operations |  |  | Preparation/Qualitrol Product/Breakers/QBCM_9a27f030.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 8 GB microSDHC standard (up to 10,000 operations records)
PROD_PDF_QBCM_QUALITROL_BREAKER_CONDITION_MONITORING | QBCM (Qualitrol Breaker Condition Monitoring) | PF_BREAKER | MET_PROTOCOL | Protocols |  |  | DNP3.0, IEC 61850, Modbus | text |  |  | Preparation/Qualitrol Product/Breakers/QBCM_9a27f030.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Protocols DNP3.0, IEC 61850, Modbus
PROD_PDF_QBCM_QUALITROL_BREAKER_CONDITION_MONITORING | QBCM (Qualitrol Breaker Condition Monitoring) | PF_BREAKER | MET_NETWORK | Communications hardware media |  |  | 1 x 10/100Base RJ-45, 1 x 100Base-FX ST, USB 2.0, RS 485 | text |  |  | Preparation/Qualitrol Product/Breakers/QBCM_9a27f030.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 1 x 10/100Base RJ-45, 1 x 100Base-FX with ST connector
PROD_PDF_QBCM_QUALITROL_BREAKER_CONDITION_MONITORING | QBCM (Qualitrol Breaker Condition Monitoring) | PF_BREAKER | MET_TIME_SYNC | Time sync inputs |  |  | NTP Standard or optional IEEE 1588 PTP | text |  |  | Preparation/Qualitrol Product/Breakers/QBCM_9a27f030.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: NTP Standard or optional IEEE 1588 PTP
PROD_PDF_QBCM_QUALITROL_BREAKER_CONDITION_MONITORING | QBCM (Qualitrol Breaker Condition Monitoring) | PF_BREAKER | MET_AMBIENT_TEMP | Ambient operating temperature | -40 | 75 | -40° C to +75° C | °C |  |  | Preparation/Qualitrol Product/Breakers/QBCM_9a27f030.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Ambient operating temperature -40° C to +75° C
PROD_PDF_QBCM_QUALITROL_BREAKER_CONDITION_MONITORING | QBCM (Qualitrol Breaker Condition Monitoring) | PF_BREAKER | MET_HUMIDITY | Humidity | 5 | 97 | 5 - 97%, non-condensing | %RH |  |  | Preparation/Qualitrol Product/Breakers/QBCM_9a27f030.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Humidity 5 - 97%, non-condensing
PROD_PDF_QBCM_QUALITROL_BREAKER_CONDITION_MONITORING | QBCM (Qualitrol Breaker Condition Monitoring) | PF_BREAKER | MET_ENCLOSURE_RATING | Enclosure rating |  |  | IP20 standard; optional IP67 for external mounting | text |  |  | Preparation/Qualitrol Product/Breakers/QBCM_9a27f030.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Enclosure rating IP20 ... Optional IP67 enclosure for external mounting
PROD_PDF_QBCM_QUALITROL_BREAKER_CONDITION_MONITORING | QBCM (Qualitrol Breaker Condition Monitoring) | PF_BREAKER | MET_POWER_SUPPLY | Rated input range |  |  | 100 - 240 V AC (50/60Hz), 110 - 250 V DC | V AC/DC |  |  | Preparation/Qualitrol Product/Breakers/QBCM_9a27f030.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Rated input range 100 - 240 V AC (50/60Hz), 110 - 250 V DC
PROD_PDF_QBCM_QUALITROL_BREAKER_CONDITION_MONITORING | QBCM (Qualitrol Breaker Condition Monitoring) | PF_BREAKER | MET_CURRENT_CHANNELS | 3-phase current channels |  | 3 | 3 channels, 0-1 V AC or 0-333mV AC split-core CTs | count |  |  | Preparation/Qualitrol Product/Breakers/QBCM_9a27f030.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 3-phase currents 3 channels, 0-1 V AC or 0-333mV AC split-core CTs
PROD_PDF_QBCM_QUALITROL_BREAKER_CONDITION_MONITORING | QBCM (Qualitrol Breaker Condition Monitoring) | PF_BREAKER | MET_COIL_CURRENT | Trip coil channels | 2 | 6 | 2-6 channels, 0-1 V DC, shunt or hall effect sensor | count |  |  | Preparation/Qualitrol Product/Breakers/QBCM_9a27f030.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Trip coils and B/U trip coils 2-6 channels, 0-1 V DC
PROD_PDF_QBCM_QUALITROL_BREAKER_CONDITION_MONITORING | QBCM (Qualitrol Breaker Condition Monitoring) | PF_BREAKER | MET_SF6_PRESSURE | SF6 gas density/pressure/humidity/dewpoint | 1 | 3 | 1-3 channel, 4-20mA analog; 1 channel RS 485 Modbus | channels |  |  | Preparation/Qualitrol Product/Breakers/QBCM_9a27f030.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: SF6 gas density/pressure/humidity/dewpoint 1-3 channel, 4-20mA for analog sensors
PROD_PDF_QBCM_QUALITROL_BREAKER_CONDITION_MONITORING | QBCM (Qualitrol Breaker Condition Monitoring) | PF_BREAKER | MET_SENSOR_TYPE | Sensor types |  |  | Split-core CT, DC Hall effect sensor, SF6 sensors, travel transducers | text |  |  | Preparation/Qualitrol Product/Breakers/QBCM_9a27f030.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: QBCM utilizes Split Core CT's ... DC hall effect sensors ... SF6 sensors
PROD_PDF_QBCM_QUALITROL_BREAKER_CONDITION_MONITORING | QBCM (Qualitrol Breaker Condition Monitoring) | PF_BREAKER | MET_VIBRATION | Mechanism travel stroke and velocity |  |  | 3 x RS 422 channels, stroke in mm/inches/degrees, velocity in m/s | text |  |  | Preparation/Qualitrol Product/Breakers/QBCM_9a27f030.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 3 x RS 422 channels on mother board, stroke measured in mm
PROD_PDF_QBCM_QUALITROL_BREAKER_CONDITION_MONITORING | QBCM (Qualitrol Breaker Condition Monitoring) | PF_BREAKER | MET_CONTACT_TYPE | Alarm relay contacts |  |  | Dry contact 5A @ 125 V AC, 3A @ 250 V AC, 0.1A @ 250 V DC | text |  |  | Preparation/Qualitrol Product/Breakers/QBCM_9a27f030.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Dry contact 5A @ 125 V AC, 3A @ 250 V AC, 0.1A @ 250 V DC
PROD_PDF_QBCM_QUALITROL_BREAKER_CONDITION_MONITORING | QBCM (Qualitrol Breaker Condition Monitoring) | PF_BREAKER | MET_TRIP_CLOSE_TIME | Mechanism operation / interruption timing |  |  | Mechanism operation time, auxiliary contact time, current interruption time | ms |  |  | Preparation/Qualitrol Product/Breakers/QBCM_9a27f030.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Mechanism operation time, auxiliary contact time, current interruption time
PROD_PDF_AKM_38750_38920_38960 | AKM 38750/38920/38960 | PF_BREAKER | MET_SF6_PRESSURE | Pressure range | -0.1 | 1 | Vacuum to 145 psi (-0.1 to 1 MPa) maximum | MPa |  |  | Preparation/Qualitrol Product/Breakers/SF6_Gas_Density_Gauges_0d311061.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Pressure range Vaccuum to 145 psi (-0.1 to 1 Mpa) maximum
PROD_PDF_AKM_38750_38920_38960 | AKM 38750/38920/38960 | PF_BREAKER | MET_CONTACT_TYPE | Switch type |  |  | Snap action SPST or SPDT (UL listed, CSA approved) | text |  |  | Preparation/Qualitrol Product/Breakers/SF6_Gas_Density_Gauges_0d311061.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Snap action – SPST or SPDT (Underwriters Laboratories Inc. listed and CSA approved)
PROD_PDF_AKM_38750_38920_38960 | AKM 38750/38920/38960 | PF_BREAKER | MET_POWER_SUPPLY | Switch rating |  |  | 3A @ 250VAC; 5A @ 125VAC; 0.5A @ 125VDC; 0.25A @ 250VDC | A/V |  |  | Preparation/Qualitrol Product/Breakers/SF6_Gas_Density_Gauges_0d311061.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 3 Amps @ 250 VAC, resistive 5 Amps @ 125 VAC
PROD_PDF_AKM_38750_38920_38960 | AKM 38750/38920/38960 | PF_BREAKER | MET_ENCLOSURE_RATING | Enclosure Class |  |  | Vented, meets IP54 (NEMA 3S) | text |  |  | Preparation/Qualitrol Product/Breakers/SF6_Gas_Density_Gauges_0d311061.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Enclosure Class Vented, meets IP54
PROD_PDF_AKM_38750_38920_38960 | AKM 38750/38920/38960 | PF_BREAKER | MET_AMBIENT_TEMP | Std. operating temperatures | -40 | 70 | -40°F to +158°F (-40°C to +70°C) | °C |  |  | Preparation/Qualitrol Product/Breakers/SF6_Gas_Density_Gauges_0d311061.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Std. operating temperatures -40°F to +158°F (-40°C to +70°C)
PROD_PDF_AKM_38750_38920_38960 | AKM 38750/38920/38960 | PF_BREAKER | MET_HUMIDITY | Ambient humidity | 5 | 95 | 5% to 95% non-condensing | %RH |  |  | Preparation/Qualitrol Product/Breakers/SF6_Gas_Density_Gauges_0d311061.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient humidity 5% to 95% non-condensing
PROD_PDF_AKM_38750_38920_38960 | AKM 38750/38920/38960 | PF_BREAKER | MET_VIBRATION | Vibration |  |  | 50/60 Hz at 0.004" displacement and 10g shock | g |  |  | Preparation/Qualitrol Product/Breakers/SF6_Gas_Density_Gauges_0d311061.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Vibration 50/60 Hz at 0.004” displacement and 10g shock
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_POWER_SUPPLY | Universal power supply |  |  | 120-240 V AC, 50/60 Hz; 125-250 V DC; <50 W | V AC/DC |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: 120 - 240 V AC, 20%; 50/60 Hz; 125 - 250 V DC
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_PROTOCOL | Communication protocols |  |  | DNP 3.0 (Level 3), Modbus, IEC 61850, IEC 60870-104-5 | text |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: DNP 3.0 (Level3), Modbus IEC 60870-104-5 IEC 61850
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_NETWORK | Network interfaces |  |  | 10/100 Ethernet TX RJ45, Ethernet FX ST, USB-A, RS-485 | text |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: 10/100 Ethernet TX, RJ45 port; USB-A port; RS-485
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_ANALOG_CHANNELS | Analog inputs per module / system | 8 | 112 | 8 per module, up to 112 per system | count |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 8 analog inputs per module; Up to 112 analog inputs per system
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_SENSOR_COUNT | Digital inputs per module / system | 14 | 196 | 14 per module, up to 196 per system | count |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 14 digital inputs per module; Up to 196 digital inputs per system
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_CONTACT_TYPE | Output relays | 8 | 112 | 8 Form C relays per module; 10A @120/240VAC; up to 112 per system | count |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: 8 Form C relays; 10 A @ 120 / 240 V AC
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_OIL_TEMPERATURE | Liquid/ambient temperature range | -40 | 120 | -40 - 120°C | °C |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: Liquid / ambient temperature range: -40 - 120°C
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_WINDING_TEMP | Winding temperature range | -40 | 200 | -40 - 200°C | °C |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: Winding temperature range: -40 - 200°C
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_SENSOR_TYPE | Fiber optic winding temperature probes | 4 | 8 | Up to 8 fiber optic input probes; available in 4,6,8 inputs | count |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Up to 8 fiber optic input probes
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_ALARM_THRESHOLD | Fiber optic accuracy |  |  | ±1°C | °C |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: ±1°C
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_BUSHING_COUNT | Bushing monitoring capacity | 3 | 6 | Up to 6 bushings (minimum 3 signals required) | count |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Up to 6 bushings (minimum 3 signals required)
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_TAN_DELTA | Tan Delta / Power Factor accuracy |  |  | Better than ±0.0001 (0.1mrad phase shift) | decimal |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Tan Delta / Power Factor: Accuracy better than ±0.0001
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_CAPACITANCE | Capacitance accuracy |  |  | Better than 0.2% | % |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Capacitance: Accuracy better than 0.2%
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_ENCLOSURE_RATING | Enclosure IP rating |  |  | IP20 (higher ratings available on request) | text |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: IP20. (Higher IP enclosure ratings available on request)
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_AMBIENT_TEMP | Operating temperature | -40 | 72 | -40°C to +72°C | °C |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Operating temperature -40°C to +72°C
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_AMBIENT_TEMP | Operating temperature (Bushing module) | -20 | 72 | -20°C to +72°C | °C |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Operating temperature (Bushing module) -20°C to +72°C
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_HUMIDITY | Operating humidity | 5 | 95 | 5 - 95% non-condensing | %RH |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: 5 - 95% non-condensing
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_ALARM_THRESHOLD | Analog input accuracy |  |  | ±0.5% full scale input range | % |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: ±0.5% full scale input range
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_SENSOR_TYPE | Temperature sensor type |  |  | 100 ohm platinum (Pt100) RTD; simulated winding | text |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: 100 ohm platinum (Pt100) RTD; simulated winding
PROD_PDF_QUALITROL_QTMS | QUALITROL QTMS | PF_TR_TEMP | MET_PD_LEVEL | Partial discharge monitoring |  |  | Ethernet port to connect 1 OCU for partial discharge monitoring | text |  |  | Preparation/Qualitrol Product/Bushings/QTMS_b041f478.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Ethernet port to connect 1 OCU for partial discharge monitoring
PROD_PDF_QUALITROL_DMS_GEN3_GEN3_PDMS | Qualitrol DMS Gen3 (Gen3 PDMS) | PF_GIS_PD | MET_SENSOR_TYPE | PD Sensor Type |  |  | UHF sensors | text |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/Gen_3_PDM_c5bdb2c6.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: utilizes a series of UHF sensors to detect PD
PROD_PDF_QUALITROL_DMS_GEN3_GEN3_PDMS | Qualitrol DMS Gen3 (Gen3 PDMS) | PF_GIS_PD | MET_SENSOR_COUNT | Max UHF PD Sensors |  | 2000 | 2,000 UHF PD Sensors | count |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/Gen_3_PDM_c5bdb2c6.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: capable of monitoring 2,000 UHF PD Sensors
PROD_PDF_QUALITROL_DMS_GEN3_GEN3_PDMS | Qualitrol DMS Gen3 (Gen3 PDMS) | PF_GIS_PD | MET_SENSOR_COUNT | Max Gas Density Sensors |  | 4000 | 4,000 Gas Density Sensors | count |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/Gen_3_PDM_c5bdb2c6.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: and 4,000 Gas Density Sensors
PROD_PDF_QUALITROL_DMS_GEN3_GEN3_PDMS | Qualitrol DMS Gen3 (Gen3 PDMS) | PF_GIS_PD | MET_PD_LEVEL | PD Sensitivity |  |  | -80 dBm | dBm |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/Gen_3_PDM_c5bdb2c6.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: industry leading sensitivity of -80 dBm
PROD_PDF_QUALITROL_DMS_GEN3_GEN3_PDMS | Qualitrol DMS Gen3 (Gen3 PDMS) | PF_GIS_PD | MET_PD_LEVEL | UHF Band Coverage | 300 | 2000 | 300 to 2,000 MHz | MHz |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/Gen_3_PDM_c5bdb2c6.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: wide band selections, covering 300 to 2,000 MHz
PROD_PDF_QUALITROL_DMS_GEN3_GEN3_PDMS | Qualitrol DMS Gen3 (Gen3 PDMS) | PF_GIS_PD | MET_ANALOG_CHANNELS | RCC Input Channels |  | 2000 | 2000 channels max, VT input and switching signals | count |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/Gen_3_PDM_c5bdb2c6.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Input 2000 channels max, VT input and switching signals
PROD_PDF_QUALITROL_DMS_GEN3_GEN3_PDMS | Qualitrol DMS Gen3 (Gen3 PDMS) | PF_GIS_PD | MET_TIME_SYNC | Time Stamping |  |  | LAN NTP signal or GPS | text |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/Gen_3_PDM_c5bdb2c6.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Time Stamping LAN NTP signal or GPS
PROD_PDF_QUALITROL_DMS_GEN3_GEN3_PDMS | Qualitrol DMS Gen3 (Gen3 PDMS) | PF_GIS_PD | MET_CONTACT_TYPE | Alarm Output Contacts |  |  | 3 standard SCADA/SCS alarm contacts and 5 configurable alarms | text |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/Gen_3_PDM_c5bdb2c6.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: 3 standard SCADA or SCS alarm contacts and additional 5 configurable alarms
PROD_PDF_QUALITROL_DMS_GEN3_GEN3_PDMS | Qualitrol DMS Gen3 (Gen3 PDMS) | PF_GIS_PD | MET_SENSOR_COUNT | OCU Input Channels |  | 7 | 7 UHF channels: 6 UHF coupler inputs + 1 external antenna | count |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/Gen_3_PDM_c5bdb2c6.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: 7 UHF channels 6 UHF coupler inputs + 1 external antenna
PROD_PDF_QUALITROL_DMS_GEN3_GEN3_PDMS | Qualitrol DMS Gen3 (Gen3 PDMS) | PF_GIS_PD | MET_PD_LEVEL | OCU Dynamic Range |  |  | Standard -75 to -30dBm; HDR -80 to -10dBm | dBm |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/Gen_3_PDM_c5bdb2c6.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Standard OCU: -75dBm to -30dBm HDR OCU: -80dBm to -10dBm
PROD_PDF_QUALITROL_DMS_GEN3_GEN3_PDMS | Qualitrol DMS Gen3 (Gen3 PDMS) | PF_GIS_PD | MET_POWER_SUPPLY | Power Supply |  |  | 110V 50/60Hz, 250mA | V AC |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/Gen_3_PDM_c5bdb2c6.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Power Supply 110V 50/60Hz, 250mA
PROD_PDF_QUALITROL_DMS_GEN3_GEN3_PDMS | Qualitrol DMS Gen3 (Gen3 PDMS) | PF_GIS_PD | MET_HUMIDITY | Humidity |  |  | 100% Condensing | %RH |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/Gen_3_PDM_c5bdb2c6.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Humidity 100% Condensing
PROD_PDF_QUALITROL_DMS_GEN3_GEN3_PDMS | Qualitrol DMS Gen3 (Gen3 PDMS) | PF_GIS_PD | MET_AMBIENT_TEMP | Operating Temperature | -25 | 55 | -25C to 55C | °C |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/Gen_3_PDM_c5bdb2c6.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Operating Temperature -25C to 55C
PROD_PDF_QUALITROL_DMS_GEN3_GEN3_PDMS | Qualitrol DMS Gen3 (Gen3 PDMS) | PF_GIS_PD | MET_PROTOCOL | Communication Protocols |  |  | IEC 61850 and Modbus | text |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/Gen_3_PDM_c5bdb2c6.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Data summary and alarms notifications through IEC 61850 and Modbus
PROD_PDF_QUALITROL_DMS_GEN3_GEN3_PDMS | Qualitrol DMS Gen3 (Gen3 PDMS) | PF_GIS_PD | MET_NETWORK | Network Interface |  |  | Remote client over Ethernet; copper or fiber | text |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/Gen_3_PDM_c5bdb2c6.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Remote client over Ethernet
PROD_PDF_QUALITROL_QPDM_SERIES | Qualitrol QPDM Series | PF_PD_TRANSFORMER | MET_SENSOR_COUNT | UHF sensor channels | 1 | 6 | 1 to 6 UHF sensor inputs | count |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/QPDM_Software_fad2476a.pdf (page 11) | Datasheet-sourced (Step 0b). Evidence: Supports 1 to 6 channels for UHF sensor inputs
PROD_PDF_QUALITROL_QPDM_SERIES | Qualitrol QPDM Series | PF_PD_TRANSFORMER | MET_SENSOR_TYPE | Sensor type |  |  | UHF (internal, window, drain valve, custom) | text |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/QPDM_Software_fad2476a.pdf (page 8) | Datasheet-sourced (Step 0b). Evidence: connected with any available UHF sensor; internal, window or drain valve
PROD_PDF_QUALITROL_QPDM_SERIES | Qualitrol QPDM Series | PF_PD_TRANSFORMER | MET_PD_LEVEL | Sensitivity |  |  | -80 dBm | dBm |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/QPDM_Software_fad2476a.pdf (page 11) | Datasheet-sourced (Step 0b). Evidence: Sensitivity -80 dBm
PROD_PDF_QUALITROL_QPDM_SERIES | Qualitrol QPDM Series | PF_PD_TRANSFORMER | MET_SAMPLING_RATE | Sample rate |  |  | 15360 samples/s per channel at 60 Hz | samples/s |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/QPDM_Software_fad2476a.pdf (page 11) | Datasheet-sourced (Step 0b). Evidence: Sample rate 15360 samples/s per channel at 60 Hz
PROD_PDF_QUALITROL_QPDM_SERIES | Qualitrol QPDM Series | PF_PD_TRANSFORMER | MET_POWER_SUPPLY | Voltage range | 90 | 264 | 90 to 264 V AC; 50/60 Hz | V AC |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/QPDM_Software_fad2476a.pdf (page 11) | Datasheet-sourced (Step 0b). Evidence: Voltage range 90 to 264 V AC; 50/60 Hz
PROD_PDF_QUALITROL_QPDM_SERIES | Qualitrol QPDM Series | PF_PD_TRANSFORMER | MET_CONTACT_TYPE | Alarm output contacts |  |  | 4 x SCADA/SCS alarm contacts for PD Warning, PD Alarm, System Fault | count |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/QPDM_Software_fad2476a.pdf (page 11) | Datasheet-sourced (Step 0b). Evidence: 4 x SCADA/SCS alarms contacts for PD Warning, PD Alarm
PROD_PDF_QUALITROL_QPDM_SERIES | Qualitrol QPDM Series | PF_PD_TRANSFORMER | MET_PROTOCOL | Output protocols |  |  | IEC61850 / Modbus | text |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/QPDM_Software_fad2476a.pdf (page 11) | Datasheet-sourced (Step 0b). Evidence: Output protocols IEC61850 / Modbus
PROD_PDF_QUALITROL_QPDM_SERIES | Qualitrol QPDM Series | PF_PD_TRANSFORMER | MET_NETWORK | Network output |  |  | Ethernet (multi/single mode fiber optic or RJ45) | text |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/QPDM_Software_fad2476a.pdf (page 11) | Datasheet-sourced (Step 0b). Evidence: Output Ethernet (multi/single mode fiber optic or RJ45)
PROD_PDF_QUALITROL_QPDM_SERIES | Qualitrol QPDM Series | PF_PD_TRANSFORMER | MET_AMBIENT_TEMP | Ambient operating temperature | -55 | 55 | -55° to +55° C | °C |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/QPDM_Software_fad2476a.pdf (page 11) | Datasheet-sourced (Step 0b). Evidence: Ambient operating temperature -55° to +55° C
PROD_PDF_QUALITROL_QPDM_SERIES | Qualitrol QPDM Series | PF_PD_TRANSFORMER | MET_HUMIDITY | Humidity | 5 | 95 | 5 to 95%, non-condensing | %RH |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/QPDM_Software_fad2476a.pdf (page 11) | Datasheet-sourced (Step 0b). Evidence: Humidity 5 to 95%, non-condensing
PROD_PDF_QUALITROL_QPDM_SERIES | Qualitrol QPDM Series | PF_PD_TRANSFORMER | MET_ENCLOSURE_RATING | Enclosure rating |  |  | IP66 | text |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/QPDM_Software_fad2476a.pdf (page 11) | Datasheet-sourced (Step 0b). Evidence: Enclosure rating IP66
PROD_PDF_IRIS_POWER_AGTRACII | Iris Power AGTracII | PF_GEN_AIRGAP | MET_SENSOR_TYPE | Air gap sensor type |  |  | Capacitive sensors (printed circuit board) | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/AGTracII_6cebaaf2.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: low profile capacitive sensors designed for accurate distance measurement
PROD_PDF_IRIS_POWER_AGTRACII | Iris Power AGTracII | PF_GEN_AIRGAP | MET_SENSOR_COUNT | Air gap sensor count | 4 | 16 | 4 to 16 sensors | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/AGTracII_6cebaaf2.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Air Gap Capacitive Sensors (4 to 16 sensors)
PROD_PDF_IRIS_POWER_AGTRACII | Iris Power AGTracII | PF_GEN_AIRGAP | MET_AIR_GAP | Linear measurement range | 2 | 50 | 2–50 mm | mm |  |  | Preparation/Qualitrol Product/Generator_Solutions/AGTracII_6cebaaf2.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Linear measurement range of the sensors is 2–50 mm
PROD_PDF_IRIS_POWER_AGTRACII | Iris Power AGTracII | PF_GEN_AIRGAP | MET_AMBIENT_TEMP | Sensor operating temperature | 0 | 125 | 0…125°C | °C |  |  | Preparation/Qualitrol Product/Generator_Solutions/AGTracII_6cebaaf2.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: OPERATING TEMP. 0…125°C
PROD_PDF_IRIS_POWER_AGTRACII | Iris Power AGTracII | PF_GEN_AIRGAP | MET_AIR_GAP | AGS-10 measurement range | 2 | 10 | 2–10mm | mm |  |  | Preparation/Qualitrol Product/Generator_Solutions/AGTracII_6cebaaf2.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: RANGE 2–10mm
PROD_PDF_IRIS_POWER_AGTRACII | Iris Power AGTracII | PF_GEN_AIRGAP | MET_AIR_GAP | AGS-15 measurement range | 3 | 15 | 3–15mm | mm |  |  | Preparation/Qualitrol Product/Generator_Solutions/AGTracII_6cebaaf2.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: RANGE 3–15mm
PROD_PDF_IRIS_POWER_AGTRACII | Iris Power AGTracII | PF_GEN_AIRGAP | MET_AIR_GAP | AGS-25 measurement range | 5 | 25 | 5–25mm | mm |  |  | Preparation/Qualitrol Product/Generator_Solutions/AGTracII_6cebaaf2.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: RANGE 5–25mm
PROD_PDF_IRIS_POWER_AGTRACII | Iris Power AGTracII | PF_GEN_AIRGAP | MET_AIR_GAP | AGS-50 measurement range | 10 | 50 | 10–50mm | mm |  |  | Preparation/Qualitrol Product/Generator_Solutions/AGTracII_6cebaaf2.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: RANGE 10–50mm
PROD_PDF_IRIS_POWER_AGTRACII | Iris Power AGTracII | PF_GEN_AIRGAP | MET_SENSOR_COUNT | Sync sensor count |  |  | 1 sensor | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/AGTracII_6cebaaf2.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Sync Sensor (1 sensor)
PROD_PDF_IRIS_POWER_AGTRACII | Iris Power AGTracII | PF_GEN_AIRGAP | MET_PROTOCOL | Communication with plant SCADA |  |  | SCADA | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/AGTracII_6cebaaf2.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Communicates with the plant SCADA system
PROD_PDF_IRIS_POWER_AGTRACII | Iris Power AGTracII | PF_GEN_AIRGAP | MET_NETWORK | Network interface |  |  | Local area network | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/AGTracII_6cebaaf2.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Provide data to a local area network
PROD_PDF_IRIS_POWER_AGTRACII | Iris Power AGTracII | PF_GEN_AIRGAP | MET_TIME_SYNC | Time synchronization |  |  | Synchronized time signals | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/AGTracII_6cebaaf2.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Set up and accept synchronized time signals
PROD_PDF_IRIS_POWER_AGTRACII | Iris Power AGTracII | PF_GEN_AIRGAP | MET_ALARM_THRESHOLD | Alarm and trip conditions |  |  | Set and provide alarm and trip conditions | varies |  |  | Preparation/Qualitrol Product/Generator_Solutions/AGTracII_6cebaaf2.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Set and provide alarm and trip conditions
PROD_PDF_IRIS_POWER_CAPACITIVE_AIR_GAP_SENSOR_CGS020210_CGP_02 | Iris Power Capacitive Air Gap Sensor CGS020210 (CGP-02) | PF_GEN_AIRGAP | MET_SENSOR_TYPE | Capacitive Air Gap Probe |  |  | CGP-02 | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Capacitive Air Gap Probe CGP-02
PROD_PDF_IRIS_POWER_CAPACITIVE_AIR_GAP_SENSOR_CGS020210_CGP_02 | Iris Power Capacitive Air Gap Sensor CGS020210 (CGP-02) | PF_GEN_AIRGAP | MET_AIR_GAP | Measuring Range | 3 | 15 | 3mm to 15mm | mm |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Measuring Range 3mm to 15mm
PROD_PDF_IRIS_POWER_CAPACITIVE_AIR_GAP_SENSOR_CGS020210_CGP_02 | Iris Power Capacitive Air Gap Sensor CGS020210 (CGP-02) | PF_GEN_AIRGAP | MET_AIR_GAP | Recommend Range for Air Gap | 5 | 12 | 5mm to 12mm | mm |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Recommend Range for Air Gap 5mm to 12mm
PROD_PDF_IRIS_POWER_CAPACITIVE_AIR_GAP_SENSOR_CGS020210_CGP_02 | Iris Power Capacitive Air Gap Sensor CGS020210 (CGP-02) | PF_GEN_AIRGAP | MET_AMBIENT_TEMP | Probe Operating Temperature | -15 | 125 | -15 oC to 125 oC | °C |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Operating Temperature - 15 oC to 125 oC
PROD_PDF_IRIS_POWER_CAPACITIVE_AIR_GAP_SENSOR_CGS020310_CGP_03 | Iris Power Capacitive Air Gap Sensor CGS020310 (CGP-03) | PF_GEN_AIRGAP | MET_SENSOR_TYPE | Capacitive Air Gap Probe |  |  | CGP-03 | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Capacitive Air Gap Probe CGP-03
PROD_PDF_IRIS_POWER_CAPACITIVE_AIR_GAP_SENSOR_CGS020310_CGP_03 | Iris Power Capacitive Air Gap Sensor CGS020310 (CGP-03) | PF_GEN_AIRGAP | MET_AIR_GAP | Measuring Range | 5 | 25 | 5mm to 25mm | mm |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Measuring Range 5mm to 25mm
PROD_PDF_IRIS_POWER_CAPACITIVE_AIR_GAP_SENSOR_CGS020310_CGP_03 | Iris Power Capacitive Air Gap Sensor CGS020310 (CGP-03) | PF_GEN_AIRGAP | MET_AIR_GAP | Recommend Range for Air Gap | 12 | 22 | 12mm to 22mm | mm |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Recommend Range for Air Gap 12mm to 22mm
PROD_PDF_IRIS_POWER_CAPACITIVE_AIR_GAP_SENSOR_CGS020410_CGP_04 | Iris Power Capacitive Air Gap Sensor CGS020410 (CGP-04) | PF_GEN_AIRGAP | MET_SENSOR_TYPE | Capacitive Air Gap Probe |  |  | CGP-04 | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Capacitive Air Gap Probe CGP-04
PROD_PDF_IRIS_POWER_CAPACITIVE_AIR_GAP_SENSOR_CGS020410_CGP_04 | Iris Power Capacitive Air Gap Sensor CGS020410 (CGP-04) | PF_GEN_AIRGAP | MET_AIR_GAP | Measuring Range | 10 | 50 | 10mm to 50mm | mm |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Measuring Range 10mm to 50mm
PROD_PDF_IRIS_POWER_CAPACITIVE_AIR_GAP_SENSOR_CGS020410_CGP_04 | Iris Power Capacitive Air Gap Sensor CGS020410 (CGP-04) | PF_GEN_AIRGAP | MET_AIR_GAP | Recommend Range for Air Gap | 22 | 47 | 22mm to 47mm | mm |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Recommend Range for Air Gap 22mm to 47mm
PROD_PDF_IRIS_POWER_CGL_LINEARIZATION_MODULE | Iris Power CGL Linearization Module | PF_GEN_AIRGAP | MET_POWER_SUPPLY | Power Input |  |  | +24Vdc, ±10%, 220mA max | V DC |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Power Input +24Vdc, ±10%, 220mA max
PROD_PDF_IRIS_POWER_CGL_LINEARIZATION_MODULE | Iris Power CGL Linearization Module | PF_GEN_AIRGAP | MET_AMBIENT_TEMP | Module Operating Temperature | -15 | 70 | -15 oC to 70 oC | °C |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Operating Temperature -15 oC to 70 oC
PROD_PDF_IRIS_POWER_CGL_LINEARIZATION_MODULE | Iris Power CGL Linearization Module | PF_GEN_AIRGAP | MET_HUMIDITY | Relative Humidity |  | 95 | 95% non condensing | %RH |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Relevative Humidity 95% non condensing
PROD_PDF_IRIS_POWER_CGL_LINEARIZATION_MODULE | Iris Power CGL Linearization Module | PF_GEN_AIRGAP | MET_ENCLOSURE_RATING | Case Protection Class |  |  | IP66 | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Case Protection Class IP66
PROD_PDF_PDTECH_DELTAMAXX | PDTech DELTAMAXX | PF_GEN_PD | MET_VOLTAGE_LEVEL | Test Voltage Range | 15 | 50 | 15/20/30/50 kV models | kV |  |  | Preparation/Qualitrol Product/Generator_Solutions/DeltaMaxx_Analyzer_6ea453b9.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 15kV (DELTAMAXX 15) 20kV 30kV 50kV
PROD_PDF_PDTECH_DELTAMAXX | PDTech DELTAMAXX | PF_GEN_PD | MET_CAPACITANCE | Reference/Coupling Capacitor |  |  | 1nF (15/20kV), 0.7nF (30kV), 0.5nF (50kV) | nF |  |  | Preparation/Qualitrol Product/Generator_Solutions/DeltaMaxx_Analyzer_6ea453b9.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 1nF nominal for 15 & 20 kV 0.7nF
PROD_PDF_PDTECH_DELTAMAXX | PDTech DELTAMAXX | PF_GEN_PD | MET_TAN_DELTA | Tan Delta Resolution |  |  | 10-5 resolution, DF uncertainty 1-2.10-4 | % / decimal |  |  | Preparation/Qualitrol Product/Generator_Solutions/DeltaMaxx_Analyzer_6ea453b9.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Tan 10-5 (resolution) Error DF 1-2.10-4
PROD_PDF_PDTECH_DELTAMAXX | PDTech DELTAMAXX | PF_GEN_PD | MET_POWER_SUPPLY | Power Supply |  |  | Via USB; PD module external 5V DC | V DC |  |  | Preparation/Qualitrol Product/Generator_Solutions/DeltaMaxx_Analyzer_6ea453b9.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Power Supply Via USB (for PD Module external power required)
PROD_PDF_PDTECH_DELTAMAXX | PDTech DELTAMAXX | PF_GEN_PD | MET_PROTOCOL | Interface |  |  | USB | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/DeltaMaxx_Analyzer_6ea453b9.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Interface USB PC requirement: Desktop or Notebook
PROD_PDF_PDTECH_DELTAMAXX | PDTech DELTAMAXX | PF_GEN_PD | MET_PD_LEVEL | PD Ranges |  |  | 10pC to 200nC typical | pC/nC |  |  | Preparation/Qualitrol Product/Generator_Solutions/DeltaMaxx_Analyzer_6ea453b9.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: PD Ranges Depends on test object 10pC to 200nC typical
PROD_PDF_PDTECH_DELTAMAXX | PDTech DELTAMAXX | PF_GEN_PD | MET_SENSOR_TYPE | Coupler Impedance |  |  | Integrated high-voltage isolation transformer | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/DeltaMaxx_Analyzer_6ea453b9.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Coupler Impedance Integrated high-voltage isolation transformer
PROD_PDF_IRIS_POWER_EL_CID_EVOLUTION | Iris Power EL CID Evolution | PF_GEN_PD | MET_ASSET_TYPE | Applicable machines |  |  | Turbine generators, hydrogenerators, and large motors | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/EL_CID_8fe18258.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: applied to turbine generators, hydrogenerators, and large motors
PROD_PDF_IRIS_POWER_EL_CID_EVOLUTION | Iris Power EL CID Evolution | PF_GEN_PD | MET_SENSOR_TYPE | Chattock sensors |  |  | Chattock Sensors (10, 20, 25 and 30 cm) | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/EL_CID_8fe18258.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Chattock Sensors (10, 20, 25 and 30 cm)
PROD_PDF_IRIS_POWER_EPOXY_MICA_CAPACITORS_EMC_80_PF | Iris Power Epoxy Mica Capacitors (EMC) 80 pF | PF_GEN_PD | MET_SENSOR_TYPE | Sensor type |  |  | Epoxy Mica Capacitor (80 pF) PD coupler | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/Epoxy_Mica_Capacitors_(EMC_Sensors)_8912f79b.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: Iris Power Epoxy Mica Capacitors (EMCs)... detect Partial Discharge (PD) activity
PROD_PDF_IRIS_POWER_EPOXY_MICA_CAPACITORS_EMC_80_PF | Iris Power Epoxy Mica Capacitors (EMC) 80 pF | PF_GEN_PD | MET_CAPACITANCE | Capacitance rating | 76 | 84 | 80 pF +/- 4 pF | pF |  |  | Preparation/Qualitrol Product/Generator_Solutions/Epoxy_Mica_Capacitors_(EMC_Sensors)_8912f79b.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Capacitance rating: 80 pF +/- 4 pF
PROD_PDF_IRIS_POWER_EPOXY_MICA_CAPACITORS_EMC_80_PF | Iris Power Epoxy Mica Capacitors (EMC) 80 pF | PF_GEN_PD | MET_VOLTAGE_LEVEL | EMC voltage rating options | 6.9 | 28 | 6.9 kV / 16 kV / 25 kV / 28 kV | kV |  |  | Preparation/Qualitrol Product/Generator_Solutions/Epoxy_Mica_Capacitors_(EMC_Sensors)_8912f79b.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: EMC Voltage Rating 6.9 kV 16 kV 25 kV 28 kV
PROD_PDF_IRIS_POWER_EPOXY_MICA_CAPACITORS_EMC_80_PF | Iris Power Epoxy Mica Capacitors (EMC) 80 pF | PF_GEN_PD | MET_PD_LEVEL | PDEV Sensitivity |  |  | 1 pC | pC |  |  | Preparation/Qualitrol Product/Generator_Solutions/Epoxy_Mica_Capacitors_(EMC_Sensors)_8912f79b.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: PDEV Sensitivity: 1 pC (ASTM D1868 and IEC 60270)
PROD_PDF_IRIS_POWER_EPOXY_MICA_CAPACITORS_EMC_80_PF | Iris Power Epoxy Mica Capacitors (EMC) 80 pF | PF_GEN_PD | MET_AMBIENT_TEMP | Operating temperature range | -50 | 130 | -50 °C to +130 °C | °C |  |  | Preparation/Qualitrol Product/Generator_Solutions/Epoxy_Mica_Capacitors_(EMC_Sensors)_8912f79b.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Operating temperature range: -50 °C to +130 °C
PROD_PDF_IRIS_POWER_EPOXY_MICA_CAPACITORS_EMC_80_PF | Iris Power Epoxy Mica Capacitors (EMC) 80 pF | PF_GEN_PD | MET_SENSOR_COUNT | Installation requirement |  |  | At least one per phase | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/Epoxy_Mica_Capacitors_(EMC_Sensors)_8912f79b.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: permanently installed, with at least one per phase
PROD_PDF_IRIS_POWER_EVAII | Iris Power EVAII | PF_GEN_EWV | MET_SENSOR_TYPE | Sensor type |  |  | Single or dual axis fiber optic accelerometer | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/EVAII_Endwinding_Vibration_Monitoring_3333c33c.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: Sensors can be of the single axis or the dual axis type
PROD_PDF_IRIS_POWER_EVAII | Iris Power EVAII | PF_GEN_EWV | MET_VIBRATION | Sensitivity |  |  | 100 mV/g | mV/g |  |  | Preparation/Qualitrol Product/Generator_Solutions/EVAII_Endwinding_Vibration_Monitoring_3333c33c.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Sensitivity 100 mV/g
PROD_PDF_IRIS_POWER_EVAII | Iris Power EVAII | PF_GEN_EWV | MET_VIBRATION | Frequency Range | 5 | 1000 | 5-1000 Hz (+/- 1 dB) | Hz |  |  | Preparation/Qualitrol Product/Generator_Solutions/EVAII_Endwinding_Vibration_Monitoring_3333c33c.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Frequency Range 5-1000 Hz (+/- 1 dB)
PROD_PDF_IRIS_POWER_EVAII | Iris Power EVAII | PF_GEN_EWV | MET_VIBRATION | Dynamic Range | 0 | 50 | 0-50 g | g |  |  | Preparation/Qualitrol Product/Generator_Solutions/EVAII_Endwinding_Vibration_Monitoring_3333c33c.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Dynamic Range 0-50 g
PROD_PDF_IRIS_POWER_EVAII | Iris Power EVAII | PF_GEN_EWV | MET_AMBIENT_TEMP | Sensor Operating Temperature | -50 | 180 | -50 ˚C to +180 ˚C | °C |  |  | Preparation/Qualitrol Product/Generator_Solutions/EVAII_Endwinding_Vibration_Monitoring_3333c33c.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Operating Temperature -50 ˚C to + 180 ˚C
PROD_PDF_IRIS_POWER_EVAII | Iris Power EVAII | PF_GEN_EWV | MET_AMBIENT_TEMP | EOD Operating Temperature | -20 | 60 | -20 ˚C to +60 ˚C | °C |  |  | Preparation/Qualitrol Product/Generator_Solutions/EVAII_Endwinding_Vibration_Monitoring_3333c33c.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Operating Temperature -20 ˚C to +60 ˚C
PROD_PDF_IRIS_POWER_EVAII | Iris Power EVAII | PF_GEN_EWV | MET_POWER_SUPPLY | EOD Power and Consumption |  |  | +12 VDC, 110 mA per driver | VDC |  |  | Preparation/Qualitrol Product/Generator_Solutions/EVAII_Endwinding_Vibration_Monitoring_3333c33c.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Power and Consumption +12 VDC, 110 mA per driver
PROD_PDF_IRIS_POWER_EVAII | Iris Power EVAII | PF_GEN_EWV | MET_SENSOR_COUNT | EOD Quantity |  |  | 1 per sensor axis | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/EVAII_Endwinding_Vibration_Monitoring_3333c33c.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Quantity 1 per sensor axis
PROD_PF_GEN_AIRGAP_01 | Iris Power TFProbe | PF_GEN_AIRGAP | MET_ROTOR_FLUX | Air gap flux rate of change measurement |  |  | Measures air gap flux rate of change to detect shorted rotor winding turns | text/relative |  |  | Preparation/Qualitrol Product/Generator_Solutions/FFProbe_-_Rotor_Flux_Monitoring_86c050b4.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: measure the air gap flux rate of change to detect shorted rotor winding turns
PROD_PF_GEN_AIRGAP_01 | Iris Power TFProbe | PF_GEN_AIRGAP | MET_AIR_GAP | Air gap size |  | 50 | less than 50 mm | mm |  |  | Preparation/Qualitrol Product/Generator_Solutions/FFProbe_-_Rotor_Flux_Monitoring_86c050b4.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: round rotor machines with air gap size less than 50 mm
PROD_PF_GEN_AIRGAP_01 | Iris Power TFProbe | PF_GEN_AIRGAP | MET_SENSOR_TYPE | Sensing element |  |  | Printed board 12 mm wide, 25 mm long, 4 mm thick affixed to stator tooth | mm |  |  | Preparation/Qualitrol Product/Generator_Solutions/FFProbe_-_Rotor_Flux_Monitoring_86c050b4.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: small printed board (12 mm wide, 25 mm long, 4 mm thick)
PROD_PF_GEN_AIRGAP_02 | Iris Power FFProbe | PF_GEN_AIRGAP | MET_ROTOR_FLUX | Air gap flux rate of change measurement |  |  | Measures air gap flux rate of change to detect shorted rotor winding turns | text/relative |  |  | Preparation/Qualitrol Product/Generator_Solutions/FFProbe_-_Rotor_Flux_Monitoring_86c050b4.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: measure the air gap flux rate of change to detect shorted rotor winding turns
PROD_PF_GEN_AIRGAP_02 | Iris Power FFProbe | PF_GEN_AIRGAP | MET_AIR_GAP | Air gap size | 50 |  | 50 mm and over | mm |  |  | Preparation/Qualitrol Product/Generator_Solutions/FFProbe_-_Rotor_Flux_Monitoring_86c050b4.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: used in turbine generators with an air gap size 50 mm and over
PROD_PF_GEN_AIRGAP_02 | Iris Power FFProbe | PF_GEN_AIRGAP | MET_SENSOR_TYPE | Mounting |  |  | Affixed to stator wedge with non-metallic pins, foldable layout | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/FFProbe_-_Rotor_Flux_Monitoring_86c050b4.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: affixed to a stator wedge with non-metallic pins
PROD_PDF_IRIS_POWER_FLUXTRACII_R_4208 | Iris Power FluxTracII-R 4208 | PF_GEN_AIRGAP | MET_SENSOR_TYPE | Compatible flux probe types |  |  | Iris Power TFProbe, FFProbe, other wedge mounted flux probes | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-R_4208_60a9f974.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Accepts signals from Iris Power TFProbe, Iris Power FFProbe, as well as other wedge mounted flux probes
PROD_PDF_IRIS_POWER_FLUXTRACII_R_4208 | Iris Power FluxTracII-R 4208 | PF_GEN_AIRGAP | MET_ROTOR_FLUX | Rotor magnetic flux monitoring |  |  | Continuous on-line rotor magnetic flux monitoring | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-R_4208_60a9f974.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: continuous on-line rotor magnetic flux monitoring system
PROD_PDF_IRIS_POWER_FLUXTRACII_R_4208 | Iris Power FluxTracII-R 4208 | PF_GEN_AIRGAP | MET_ASSET_COUNT | Machines monitored |  | 4 | Monitors up to four machines | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-R_4208_60a9f974.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Monitors up to four machines
PROD_PDF_IRIS_POWER_FLUXTRACII_R_4208 | Iris Power FluxTracII-R 4208 | PF_GEN_AIRGAP | MET_CONTACT_TYPE | Alarm relay contact |  |  | Relay contact to alert user of shorts | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-R_4208_60a9f974.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Provides relay contact to alert user of shorts
PROD_PDF_IRIS_POWER_FLUXTRACII_R_4208 | Iris Power FluxTracII-R 4208 | PF_GEN_AIRGAP | MET_PROTOCOL | Communication protocol |  |  | Modbus TCP/IP with server and client capability | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-R_4208_60a9f974.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Modbus TCP/IP protocol available for built-in server and client capability
PROD_PDF_IRIS_POWER_FLUXTRACII_R_4208 | Iris Power FluxTracII-R 4208 | PF_GEN_AIRGAP | MET_NETWORK | Communication ports |  |  | USB, Ethernet | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-R_4208_60a9f974.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Multiple communication ports: USB, Ethernet
PROD_PDF_IRIS_POWER_FLUXTRACII_R_4208 | Iris Power FluxTracII-R 4208 | PF_GEN_AIRGAP | MET_SENSOR_TYPE | Shaft sync (Keyphasor) input |  |  | Inputs for shaft sync sensor (Keyphasor) for slot determination | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-R_4208_60a9f974.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Inputs for shaft sync sensor (Keyphasor) for slot determination when shorts are detected
PROD_PDF_IRIS_POWER_FLUXTRACII_R_4208 | Iris Power FluxTracII-R 4208 | PF_GEN_AIRGAP | MET_AIR_GAP | FFProbe airgap requirement | 50 |  | For generators with airgap >50mm | mm |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-R_4208_60a9f974.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: For generators with airgap >50mm, Qualitrol Iris Power provides the foldable FFProbe
PROD_PDF_IRIS_POWER_FLUXTRACII_R_4208 | Iris Power FluxTracII-R 4208 | PF_GEN_AIRGAP | MET_SF6_PRESSURE | Hydrogen penetration kit test pressure |  |  | 2700 kPA or 400 PSI | kPa/PSI |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-R_4208_60a9f974.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: nitrogen gas pressure tested to 2700 kPA or 400 PSI
PROD_PDF_FLUXTRACII_S_4208 | FluxTracII-S 4208 | PF_GEN_AIRGAP | MET_GENERATOR_COUNT | Machines monitored |  | 4 | up to four machines | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-S_4208_39a21cdd.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: can monitor and evaluate up to four machines at the same time
PROD_PDF_FLUXTRACII_S_4208 | FluxTracII-S 4208 | PF_GEN_AIRGAP | MET_SENSOR_COUNT | Poles monitored per machine | 4 | 128 | 4 to 128 poles per machine | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-S_4208_39a21cdd.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Monitors 4 to 128 poles per machine
PROD_PDF_FLUXTRACII_S_4208 | FluxTracII-S 4208 | PF_GEN_AIRGAP | MET_SENSOR_TYPE | Flux probe sensor |  |  | Iris Power TFProbe / Total Flux Probe | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-S_4208_39a21cdd.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: The preferred sensor is an Iris Power TFProbe
PROD_PDF_FLUXTRACII_S_4208 | FluxTracII-S 4208 | PF_GEN_AIRGAP | MET_ROTOR_FLUX | Rotor flux monitoring |  |  | continuous on-line rotor flux monitor | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-S_4208_39a21cdd.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: continuous on-line rotor flux monitor for rotor winding shorted turn detection
PROD_PDF_FLUXTRACII_S_4208 | FluxTracII-S 4208 | PF_GEN_AIRGAP | MET_PROTOCOL | Communication protocol |  |  | Modbus TCP/IP | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-S_4208_39a21cdd.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: automatically transmitted through Modbus TCP/IP protocol to a plant SCADA system
PROD_PDF_FLUXTRACII_S_4208 | FluxTracII-S 4208 | PF_GEN_AIRGAP | MET_NETWORK | Communication ports |  |  | USB, Ethernet | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-S_4208_39a21cdd.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Multiple communication ports: USB, Ethernet
PROD_PDF_FLUXTRACII_S_4208 | FluxTracII-S 4208 | PF_GEN_AIRGAP | MET_CONTACT_TYPE | Alert relay contact |  |  | relay contact to alert user | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/FluxTracII-S_4208_39a21cdd.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Provides relay contact to alert user
PROD_PF_GEN_EWV_02 | GuardII+ | PF_GEN_PD | MET_SENSOR_TYPE | PD Sensor Type |  |  | Epoxy Mica Capacitors (EMC) and Stator Slot Couplers (SSC) | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/GuardII+_fcc4ac4b.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Epoxy Mica Capacitors (EMC) and Stator Slot Couplers (SSC) are high frequency sensors
PROD_PF_GEN_EWV_02 | GuardII+ | PF_GEN_PD | MET_SENSOR_COUNT | PD Sensor Count per Machine | 3 | 24 | 3 to 24 sensors per machine | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/GuardII+_fcc4ac4b.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: vary from 3 to 24 sensors per machine
PROD_PF_GEN_EWV_02 | GuardII+ | PF_GEN_PD | MET_PD_LEVEL | Partial Discharge Monitoring |  |  | Detects Partial Discharges within stator windings | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/GuardII+_fcc4ac4b.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: used to detect Partial Discharges (PD) occurring within stator windings
PROD_PF_GEN_EWV_02 | GuardII+ | PF_GEN_PD | MET_SENSOR_TYPE | Endwinding Vibration Sensor Type |  |  | Non-metallic fiber optic accelerometers | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/GuardII+_fcc4ac4b.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: non-metallic ﬁber optic accelerometers used to measure vibration
PROD_PF_GEN_EWV_02 | GuardII+ | PF_GEN_PD | MET_VIBRATION | Endwinding Vibration Measurement |  |  | Radial and tangential directions | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/GuardII+_fcc4ac4b.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: simultaneously measure vibration in the radial and tangential directions
PROD_PF_GEN_EWV_02 | GuardII+ | PF_GEN_PD | MET_ROTOR_FLUX | Rotor Flux Sensing |  |  | Detects shorted rotor windings by measuring air gap magnetic flux | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/GuardII+_fcc4ac4b.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: detects shorted rotor windings...by measuring air gap magnetic ﬂux
PROD_PF_GEN_EWV_02 | GuardII+ | PF_GEN_PD | MET_SENSOR_TYPE | Shaft Voltage and Current Brushes |  |  | Grounding brushes with shunts and voltage brushes | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/GuardII+_fcc4ac4b.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: grounding brush(es) are equipped with shunt(s) to measure current
PROD_PF_GEN_EWV_02 | GuardII+ | PF_GEN_PD | MET_ENCLOSURE_RATING | Enclosure Rating |  |  | IP66 | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/GuardII+_fcc4ac4b.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Rugged enclosure and connectors with IP66 rating
PROD_PF_GEN_EWV_02 | GuardII+ | PF_GEN_PD | MET_PROTOCOL | Communication Protocol |  |  | Modbus and other communication protocols | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/GuardII+_fcc4ac4b.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Built-in support for Modbus and other communication protocols
PROD_PF_GEN_EWV_02 | GuardII+ | PF_GEN_PD | MET_NETWORK | Communication Ports |  |  | USB, RJ45 and fiber optic (optional) | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/GuardII+_fcc4ac4b.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Multiple communication ports such as USB, RJ45 and ﬁber optic (optional)
PROD_PF_GEN_EWV_02 | GuardII+ | PF_GEN_PD | MET_CONTACT_TYPE | Alarm Output |  |  | LED indicators and relay output for alert notifications | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/GuardII+_fcc4ac4b.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: LED indicators and relay output for alert notiﬁcations
PROD_PDF_IRIS_POWER_MDSP3 | Iris Power MDSP3 | PF_MOTOR | MET_SENSOR_TYPE | Current sensor |  |  | Single clamp-on current sensor connected to CT secondary or phase lead | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/MDSP3_aee0c628.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: single clamp-on current sensor connected to the secondary side
PROD_PDF_IRIS_POWER_MDSP3 | Iris Power MDSP3 | PF_MOTOR | MET_SENSOR_COUNT | Current probes included |  |  | 2 | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/MDSP3_aee0c628.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: MDSP3 includes two current probes to cover a wider range
PROD_PDF_IRIS_POWER_MDSP3 | Iris Power MDSP3 | PF_MOTOR | MET_CURRENT_CHANNELS | Stator current range | 5 | 1000 | 5A to 1000A | A |  |  | Preparation/Qualitrol Product/Generator_Solutions/MDSP3_aee0c628.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: wider range of stator current from 5A to 1000A
PROD_PDF_IRIS_POWER_MDSP3 | Iris Power MDSP3 | PF_MOTOR | MET_SAMPLING_RATE | Sampling rate |  |  | >6500/sec | samples/sec |  |  | Preparation/Qualitrol Product/Generator_Solutions/MDSP3_aee0c628.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Sampling rate >6500/sec
PROD_PDF_IRIS_POWER_MDSP3 | Iris Power MDSP3 | PF_MOTOR | MET_POWER_RATING | Motor HP |  |  | 50hp (37.5kW) & up | HP/kW |  |  | Preparation/Qualitrol Product/Generator_Solutions/MDSP3_aee0c628.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Motor HP 50hp (37.5kW) & up
PROD_PDF_IRIS_POWER_MDSP3 | Iris Power MDSP3 | PF_MOTOR | MET_POWER_SUPPLY | Power supply |  |  | USB or 100 to 200 V 50/60 Hz; universal 120/240 V | V AC |  |  | Preparation/Qualitrol Product/Generator_Solutions/MDSP3_aee0c628.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: powered through the USB connection... or a 100 to 200 V 50/60 Hz power supply
PROD_PDF_IRIS_POWER_MDSP3 | Iris Power MDSP3 | PF_MOTOR | MET_ENCLOSURE_RATING | Carrying case rating |  |  | IP67, NEMA 4X | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/MDSP3_aee0c628.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Carrying case (IP67, NEMA 4X)
PROD_PDF_IRIS_POWER_PDA_IV | Iris Power PDA-IV | PF_GEN_PD | MET_PD_LEVEL | Pulse Amplitude Range | 2 | 34000 | 2 mV - 34,000 mV | mV |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDA-IV_e8515c86.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Pulse Amplitude Range 2 mV - 34,000 mV
PROD_PDF_IRIS_POWER_PDA_IV | Iris Power PDA-IV | PF_GEN_PD | MET_SENSOR_COUNT | Sensor Inputs |  |  | 12 Sensor Inputs | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDA-IV_e8515c86.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 80 pF EMC (6.9kV to 35 kV) 12 Sensor Inputs
PROD_PDF_IRIS_POWER_PDA_IV | Iris Power PDA-IV | PF_GEN_PD | MET_SENSOR_TYPE | Sensor Compatibility |  |  | 80 pF EMC (6.9kV to 35 kV) | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDA-IV_e8515c86.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Sensor Compatibility 80 pF EMC (6.9kV to 35 kV)
PROD_PDF_IRIS_POWER_PDA_IV | Iris Power PDA-IV | PF_GEN_PD | MET_AMBIENT_TEMP | Operating Temperature | -15 | 45 | -15º C to 45º C | °C |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDA-IV_e8515c86.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Operating Temperature -15º C to 45º C
PROD_PDF_IRIS_POWER_PDA_IV | Iris Power PDA-IV | PF_GEN_PD | MET_HUMIDITY | Relative Humidity |  | 95 | Up to 95% non-condensing | %RH |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDA-IV_e8515c86.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Relative Humidity Up to 95% non-condensing
PROD_PDF_IRIS_POWER_PDA_IV | Iris Power PDA-IV | PF_GEN_PD | MET_POWER_SUPPLY | Power Supply |  |  | 12V battery pack | V DC |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDA-IV_e8515c86.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Ability to operate instrument from 12V battery pack
PROD_PDF_IRIS_POWER_PDA_IV | Iris Power PDA-IV | PF_GEN_PD | MET_PROTOCOL | Communication Interface |  |  | USB or Ethernet cable | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDA-IV_e8515c86.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: control computer... using a USB or Ethernet cable
PROD_PDF_IRIS_POWER_PDTRACII_4208 | Iris Power PDTracII 4208 | PF_MOTOR | MET_VOLTAGE_LEVEL | Voltage rating |  | 35 | up to 35 kV | kV |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDTracII_08f5c95a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: switchgear, and dry type transformers rated up to 35 kV
PROD_PDF_IRIS_POWER_PDTRACII_4208 | Iris Power PDTracII 4208 | PF_MOTOR | MET_SENSOR_TYPE | PD Sensor |  |  | 80 pF EMC capacitive couplers | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDTracII_08f5c95a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 80 pF EMC (6.9 kV - 35 kV)
PROD_PDF_IRIS_POWER_PDTRACII_4208 | Iris Power PDTracII 4208 | PF_MOTOR | MET_SENSOR_COUNT | Sensor inputs |  |  | 3 | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDTracII_08f5c95a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 3 Sensor Inputs
PROD_PDF_IRIS_POWER_PDTRACII_4208 | Iris Power PDTracII 4208 | PF_MOTOR | MET_PD_LEVEL | Pulse Amplitude | 2 | 34000 | 2 mV - 34,000 mV | mV |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDTracII_08f5c95a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Pulse Amplitude 2 mV - 34,000 mV
PROD_PDF_IRIS_POWER_PDTRACII_4208 | Iris Power PDTracII 4208 | PF_MOTOR | MET_AMBIENT_TEMP | Operating Temperature | 0 | 55 | 0°C to 55°C | °C |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDTracII_08f5c95a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Operating Temperature 0°C to 55°C
PROD_PDF_IRIS_POWER_PDTRACII_4208 | Iris Power PDTracII 4208 | PF_MOTOR | MET_HUMIDITY | Relative Humidity |  | 95 | Up to 95% non-condensing | %RH |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDTracII_08f5c95a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Relative Humidity Up to 95% non-condensing
PROD_PDF_IRIS_POWER_PDTRACII_4208 | Iris Power PDTracII 4208 | PF_MOTOR | MET_ENCLOSURE_RATING | Enclosure Rating |  |  | stainless steel IP66 enclosure | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDTracII_08f5c95a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: stainless steel IP66 enclosure
PROD_PDF_IRIS_POWER_PDTRACII_4208 | Iris Power PDTracII 4208 | PF_MOTOR | MET_PROTOCOL | Networking Capability |  |  | Modbus over Ethernet (TCP/IP) | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDTracII_08f5c95a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Networking Capability Modbus over Ethernet (TCP/IP)
PROD_PDF_IRIS_POWER_PDTRACII_4208 | Iris Power PDTracII 4208 | PF_MOTOR | MET_NETWORK | Manual Data Download |  |  | USB Memory Stick | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDTracII_08f5c95a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Manual Data Download USB Memory Stick
PROD_PDF_IRIS_POWER_PDTRACII_4208 | Iris Power PDTracII 4208 | PF_MOTOR | MET_SENSOR_TYPE | Ambient Sensors |  |  | Ambient Humidity and Temperature Sensor | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDTracII_08f5c95a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Ambient Humidity Sensor Ambient Temperature Sensor
PROD_PDF_IRIS_POWER_PDTRACII_4208 | Iris Power PDTracII 4208 | PF_MOTOR | MET_ANALOG_CHANNELS | Remote analog inputs |  |  | 8 analog points | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDTracII_08f5c95a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Remote inputs with 8 analog points
PROD_PDF_IRIS_POWER_CORONA_PROBE_MODEL_PPM_97 | Iris Power Corona Probe Model PPM-97 | PF_GEN_PD | MET_SENSOR_TYPE | Sensor Type |  |  | Ferrite probe | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/PPM-97_Corona_Probe_9c7539d3.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: with its ferrite probe, is designed to measure partial discharge pulses
PROD_PDF_IRIS_POWER_CORONA_PROBE_MODEL_PPM_97 | Iris Power Corona Probe Model PPM-97 | PF_GEN_PD | MET_PD_LEVEL | Measurement Ranges |  |  | 10 / 30 / 100 / 300 / 1000 mA | mA |  |  | Preparation/Qualitrol Product/Generator_Solutions/PPM-97_Corona_Probe_9c7539d3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Ranges 10 / 30 / 100 / 300 / 1000 mA
PROD_PDF_IRIS_POWER_CORONA_PROBE_MODEL_PPM_97 | Iris Power Corona Probe Model PPM-97 | PF_GEN_PD | MET_NETWORK | Input Connection |  |  | BNC receptacle | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/PPM-97_Corona_Probe_9c7539d3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Input Connection BNC receptacle
PROD_PDF_IRIS_POWER_CORONA_PROBE_MODEL_PPM_97 | Iris Power Corona Probe Model PPM-97 | PF_GEN_PD | MET_POWER_SUPPLY | Batteries |  |  | 9V long-life (2) | V |  |  | Preparation/Qualitrol Product/Generator_Solutions/PPM-97_Corona_Probe_9c7539d3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Batteries 9V long-life (2)
PROD_PDF_QCM_PPDM | QCM-PPDM | PF_PD_TRANSFORMER | MET_POWER_SUPPLY | Voltage range |  |  | 90 to 264 VAC, 47-63 Hz; 40 to 290 VDC universal supply | V AC/DC |  |  | Preparation/Qualitrol Product/Generator_Solutions/QPPDM_2ca3bb9a.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: 90 to 264 VAC, 47-63 Hz; 40 to 290 VDC universal supply
PROD_PDF_QCM_PPDM | QCM-PPDM | PF_PD_TRANSFORMER | MET_SENSOR_COUNT | UHF channels |  |  | 6 UHF channels + 1 noise antenna channel | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/QPPDM_2ca3bb9a.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: 6 UHF channels; 1 additional channel for noise antenna
PROD_PDF_QCM_PPDM | QCM-PPDM | PF_PD_TRANSFORMER | MET_SENSOR_TYPE | Sensor type |  |  | UHF sensors | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/QPPDM_2ca3bb9a.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: UHF sensors (optional)
PROD_PDF_QCM_PPDM | QCM-PPDM | PF_PD_TRANSFORMER | MET_PD_LEVEL | Sensitivity |  |  | > 6 mm, < 5pC (-75 dBm) | pC / dBm |  |  | Preparation/Qualitrol Product/Generator_Solutions/QPPDM_2ca3bb9a.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: Outstanding sensitivity and unique accuracy (75 dBm / 5pC)
PROD_PDF_QCM_PPDM | QCM-PPDM | PF_PD_TRANSFORMER | MET_SAMPLING_RATE | Sample rate |  |  | 15.4 KS/s per channel; 107.5 KS/s total for 7 channels | samples/s |  |  | Preparation/Qualitrol Product/Generator_Solutions/QPPDM_2ca3bb9a.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: 15.4 KS/s per channel; Total of 107.5 KS/s for 7 channels
PROD_PDF_QCM_PPDM | QCM-PPDM | PF_PD_TRANSFORMER | MET_TIME_SYNC | Time synchronization |  |  | NTP / SNTP; 1 ms accuracy | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/QPPDM_2ca3bb9a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Built-in time synchronization through NTP / SNTP
PROD_PDF_QCM_PPDM | QCM-PPDM | PF_PD_TRANSFORMER | MET_NETWORK | Ethernet ports |  |  | RJ45 (10/100 Mbps) | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/QPPDM_2ca3bb9a.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: RJ45 (10/100 Mbps)
PROD_PDF_QCM_PPDM | QCM-PPDM | PF_PD_TRANSFORMER | MET_PROTOCOL | GPRS |  |  | Optional GPRS | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/QPPDM_2ca3bb9a.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: GPRS Optional
PROD_PDF_QCM_PPDM | QCM-PPDM | PF_PD_TRANSFORMER | MET_AMBIENT_TEMP | Ambient operating temperature | -25 | 55 | -25ºC to +55ºC | °C |  |  | Preparation/Qualitrol Product/Generator_Solutions/QPPDM_2ca3bb9a.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: -25ºC to +55ºC
PROD_PDF_QCM_PPDM | QCM-PPDM | PF_PD_TRANSFORMER | MET_HUMIDITY | Humidity | 5 | 95 | 5 - 95% non-condensing | %RH |  |  | Preparation/Qualitrol Product/Generator_Solutions/QPPDM_2ca3bb9a.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: 5 - 95% non-condensing
PROD_PDF_QCM_PPDM | QCM-PPDM | PF_PD_TRANSFORMER | MET_ENCLOSURE_RATING | Enclosure rating |  |  | NEMA IP66 | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/QPPDM_2ca3bb9a.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: NEMA IP66
PROD_PDF_QCM_PPDM | QCM-PPDM | PF_PD_TRANSFORMER | MET_ALARM_THRESHOLD | PD alarms |  |  | PD fault alarm, PD alarm, PD warning alarm, system status | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/QPPDM_2ca3bb9a.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: PD fault alarm - PD alarm - PD warning alarm
PROD_PDF_IRIS_POWER_RFAII_R | Iris Power RFAII-R | PF_GEN_AIRGAP | MET_ROTOR_FLUX | Rotor flux measurement |  |  | On-line rotor winding flux monitoring for shorted turns | text/relative |  |  | Preparation/Qualitrol Product/Generator_Solutions/RFAII-R_c16db884.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: On-line rotor winding flux monitoring is an essential Condition Based Maintenance tool
PROD_PDF_IRIS_POWER_RFAII_R | Iris Power RFAII-R | PF_GEN_AIRGAP | MET_AMBIENT_TEMP | Operating temperature | 0 | 40 | 0 ºC to 40 ºC | °C |  |  | Preparation/Qualitrol Product/Generator_Solutions/RFAII-R_c16db884.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Temperature (operating/storage): 0 ºC to 40 ºC
PROD_PDF_IRIS_POWER_RFAII_R | Iris Power RFAII-R | PF_GEN_AIRGAP | MET_AMBIENT_TEMP | Storage temperature | -20 | 50 | -20 ºC to 50 ºC | °C |  |  | Preparation/Qualitrol Product/Generator_Solutions/RFAII-R_c16db884.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 0 ºC to 40 ºC/-20 ºC to 50 ºC
PROD_PDF_IRIS_POWER_RFAII_R | Iris Power RFAII-R | PF_GEN_AIRGAP | MET_HUMIDITY | Relative humidity |  | 90 | <90 % non-condensing | %RH |  |  | Preparation/Qualitrol Product/Generator_Solutions/RFAII-R_c16db884.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Relative humidity: <90 % non-condensing
PROD_PDF_IRIS_POWER_RFAII_R | Iris Power RFAII-R | PF_GEN_AIRGAP | MET_POWER_SUPPLY | Power source voltage |  |  | 115/230 V, 50/60 Hz | V |  |  | Preparation/Qualitrol Product/Generator_Solutions/RFAII-R_c16db884.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Voltage: 115/230 V, 50/60 Hz
PROD_PDF_IRIS_POWER_RFAII_R | Iris Power RFAII-R | PF_GEN_AIRGAP | MET_NETWORK | Communications interfaces |  |  | USB Port (type B), Ethernet Port (RJ45) | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/RFAII-R_c16db884.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: USB Port (type B connector), Ethernet Port (RJ45)
PROD_PDF_IRIS_POWER_RFAII_R | Iris Power RFAII-R | PF_GEN_AIRGAP | MET_SENSOR_TYPE | Compatible flux probes |  |  | Iris Power FFProbe, TFProbe and older style flux probes | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/RFAII-R_c16db884.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Usable with the Iris Power FFProbe, TFProbe and older style flux probes
PROD_PDF_IRIS_POWER_RFAII_S | Iris Power RFAII-S | PF_GEN_AIRGAP | MET_ROTOR_FLUX | Flux signal input range | 0.3 | 48 | 0.3 V to 48 V | V |  |  | Preparation/Qualitrol Product/Generator_Solutions/RFAII-S_551dd1fa.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Signal range: 0.3 V to 48 V
PROD_PDF_IRIS_POWER_RFAII_S | Iris Power RFAII-S | PF_GEN_AIRGAP | MET_SENSOR_TYPE | Flux probe compatibility |  |  | Iris Power FFProbe, TFProbe and older style flux probes | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/RFAII-S_551dd1fa.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Usable with the Iris Power FFProbe, TFProbe and older style flux probes
PROD_PDF_IRIS_POWER_RFAII_S | Iris Power RFAII-S | PF_GEN_AIRGAP | MET_POWER_SUPPLY | Power source voltage |  |  | 115/230 V, 50/60 Hz | V AC |  |  | Preparation/Qualitrol Product/Generator_Solutions/RFAII-S_551dd1fa.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Voltage: 115/230 V, 50/60 Hz
PROD_PDF_IRIS_POWER_RFAII_S | Iris Power RFAII-S | PF_GEN_AIRGAP | MET_NETWORK | Communications interfaces |  |  | USB Port (type B), Ethernet Port (RJ45) | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/RFAII-S_551dd1fa.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: USB Port (type B connector), Ethernet Port (RJ45)
PROD_PDF_IRIS_POWER_RFAII_S | Iris Power RFAII-S | PF_GEN_AIRGAP | MET_AMBIENT_TEMP | Operating temperature | 0 | 40 | 0 ºC to 40 ºC | °C |  |  | Preparation/Qualitrol Product/Generator_Solutions/RFAII-S_551dd1fa.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Temperature (operating/storage): 0 ºC to 40 ºC
PROD_PDF_IRIS_POWER_RFAII_S | Iris Power RFAII-S | PF_GEN_AIRGAP | MET_HUMIDITY | Relative humidity |  | 90 | <90 % non-condensing | %RH |  |  | Preparation/Qualitrol Product/Generator_Solutions/RFAII-S_551dd1fa.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Relative humidity: <90 % non-condensing
PROD_PDF_IRIS_POWER_RIV_800 | Iris Power RIV 800 | PF_GEN_PD | MET_SENSOR_TYPE | Guidance |  |  | Automatic, Using Magnetic Sensors | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/Robotic_Inspection_Vehicle_&_Camera_System_5c0af922.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Guidance Automatic, Using Magnetic Sensors
PROD_PDF_IRIS_POWER_RIV_800 | Iris Power RIV 800 | PF_GEN_PD | MET_POWER_SUPPLY | Power Requirement | 85 | 264 | 85 - 264 V, 50/60 Hz | V AC |  |  | Preparation/Qualitrol Product/Generator_Solutions/Robotic_Inspection_Vehicle_&_Camera_System_5c0af922.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Power Requirement 85 - 264 V, 50/60 Hz
PROD_PDF_IRIS_POWER_RIV_800 | Iris Power RIV 800 | PF_GEN_PD | MET_AMBIENT_TEMP | Operating Temperature | 0 | 50 | 0° to +50°C | °C |  |  | Preparation/Qualitrol Product/Generator_Solutions/Robotic_Inspection_Vehicle_&_Camera_System_5c0af922.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Operating Temperature 0° to +50°C (+32° to +122°F)
PROD_PDF_IRIS_POWER_STATOR_SLOT_COUPLERS_SSC | Iris Power Stator Slot Couplers (SSC) | PF_GEN_PD | MET_SENSOR_TYPE | Sensor material |  |  | Epoxy glass laminate, NEMA FR4 (Class F) | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/Stator_Slot_Couplers_(SSC)_bb887587.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Material Epoxy glass laminate, NEMA FR4 (Class F)
PROD_PDF_IRIS_POWER_STATOR_SLOT_COUPLERS_SSC | Iris Power Stator Slot Couplers (SSC) | PF_GEN_PD | MET_SENSOR_COUNT | SSCs per generator | 6 |  | 6 SSCs for up to 600 MVA; more for higher rated | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/Stator_Slot_Couplers_(SSC)_bb887587.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: generators rated up to 600 MVA normally require 6 SSCs
PROD_PDF_IRIS_POWER_STATOR_SLOT_COUPLERS_SSC | Iris Power Stator Slot Couplers (SSC) | PF_GEN_PD | MET_POWER_RATING | Generator rating |  | 600 | up to 600 MVA | MVA |  |  | Preparation/Qualitrol Product/Generator_Solutions/Stator_Slot_Couplers_(SSC)_bb887587.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: Turbine generators rated up to 600 MVA normally require 6 SSCs
PROD_PDF_IRIS_POWER_SWA_STATOR_WEDGE_ANALYZER | Iris Power SWA (Stator Wedge Analyzer) | PF_MOTOR | MET_ASSET_TYPE | Applicable machinery |  |  | Motors and generators / all rotating machinery | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/Stator_Wedge_Analyzer_(SWA)_ea20c256.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: test most types of generator and motor stator slot wedges
PROD_PDF_IRIS_POWER_SWA_STATOR_WEDGE_ANALYZER | Iris Power SWA (Stator Wedge Analyzer) | PF_MOTOR | MET_SENSOR_TYPE | Sensor type |  |  | Accelerometer | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/Stator_Wedge_Analyzer_(SWA)_ea20c256.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: An accelerometer gathers the data and transmits it
PROD_PDF_IRIS_POWER_SWA_STATOR_WEDGE_ANALYZER | Iris Power SWA (Stator Wedge Analyzer) | PF_MOTOR | MET_POWER_SUPPLY | Power Supply |  |  | 90-132/180-264 V, 50/60 Hz | V AC |  |  | Preparation/Qualitrol Product/Generator_Solutions/Stator_Wedge_Analyzer_(SWA)_ea20c256.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Power Supply 90-132/180-264 V, 50/60 Hz
PROD_PDF_IRIS_POWER_SWA_STATOR_WEDGE_ANALYZER | Iris Power SWA (Stator Wedge Analyzer) | PF_MOTOR | MET_AMBIENT_TEMP | Operating Temperature | 10 | 40 | +10° to +40 °C | °C |  |  | Preparation/Qualitrol Product/Generator_Solutions/Stator_Wedge_Analyzer_(SWA)_ea20c256.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Operating Temperature +10° to +40 °C
PROD_PDF_IRIS_POWER_TGA_B | Iris Power TGA-B | PF_GEN_PD | MET_SENSOR_TYPE | Sensor Compatibility |  |  | 80 pF EMC (6.9kV - 35 kV) and/or SSC's | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-B_b099cbd2.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 80 pF EMC (6.9kV - 35 kV) and/or SSC's
PROD_PDF_IRIS_POWER_TGA_B | Iris Power TGA-B | PF_GEN_PD | MET_PD_LEVEL | Pulse Amplitude Range | 2 | 34000 | 2 mV - 34,000 mV | mV |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-B_b099cbd2.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Pulse Amplitude Range 2 mV - 34,000 mV
PROD_PDF_IRIS_POWER_TGA_B | Iris Power TGA-B | PF_GEN_PD | MET_AMBIENT_TEMP | Operating Temperature | -15 | 45 | -15ºC to 45ºC | °C |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-B_b099cbd2.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Operating Temperature -15ºC to 45ºC ( 5ºF to 113ºF )
PROD_PDF_IRIS_POWER_TGA_B | Iris Power TGA-B | PF_GEN_PD | MET_HUMIDITY | Relative Humidity |  | 95 | Up to 95% non-condensing | %RH |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-B_b099cbd2.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Relative Humidity Up to 95% non-condensing
PROD_PDF_IRIS_POWER_TGA_B | Iris Power TGA-B | PF_GEN_PD | MET_SENSOR_TYPE | Ambient Sensors |  |  | Built in Ambient Temperature Sensor and Ambient Humidity Sensor | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-B_b099cbd2.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Built in Ambient Temperature Sensor and Ambient Humidity Sensor
PROD_PDF_IRIS_POWER_TGA_B | Iris Power TGA-B | PF_GEN_PD | MET_POWER_SUPPLY | Power Supply |  |  | 12V battery pack | V |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-B_b099cbd2.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Ability to operate instrument from 12V battery pack
PROD_PDF_IRIS_POWER_TGA_B | Iris Power TGA-B | PF_GEN_PD | MET_PROTOCOL | Communication Interface |  |  | USB or Ethernet | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-B_b099cbd2.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: connected to a control computer... using a USB or Ethernet cable
PROD_PF_GEN_PD_02 | TGA-S | PF_GEN_PD | MET_SENSOR_TYPE | Sensor Compatibility |  |  | 80 pF EMC (6.9kV - 35 kV) and/or SSC's | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-S_c922447e.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 80 pF EMC (6.9kV - 35 kV) and/or SSC's
PROD_PF_GEN_PD_02 | TGA-S | PF_GEN_PD | MET_PD_LEVEL | Pulse Amplitude Range | 2 | 34000 | 2 mV - 34,000 mV | mV |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-S_c922447e.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Pulse Amplitude Range 2 mV - 34,000 mV
PROD_PF_GEN_PD_02 | TGA-S | PF_GEN_PD | MET_AMBIENT_TEMP | Operating Temperature | -15 | 45 | -15ºC to 45ºC | °C |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-S_c922447e.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Operating Temperature -15ºC to 45ºC
PROD_PF_GEN_PD_02 | TGA-S | PF_GEN_PD | MET_HUMIDITY | Relative Humidity |  | 95 | Up to 95% non-condensing | %RH |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-S_c922447e.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Relative Humidity Up to 95% non-condensing
PROD_PF_GEN_PD_02 | TGA-S | PF_GEN_PD | MET_POWER_SUPPLY | Battery Operation |  |  | 12V battery pack | V |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-S_c922447e.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Ability to operate instrument from 12V battery pack
PROD_PF_GEN_PD_02 | TGA-S | PF_GEN_PD | MET_NETWORK | Computer Interface |  |  | USB or Ethernet cable | text |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-S_c922447e.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: control computer... using a USB or Ethernet cable
PROD_PDF_QUALITROL_CORE_PACKAGE | Qualitrol Core Package | PF_DGA | MET_DGA_GAS_SPECIES | Measured gas |  |  | Hydrogen only | text |  |  | Preparation/Qualitrol Product/Software_Solutions/Core_Package_02229adb.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Responds only to Hydrogen: no cross interfernece or composite measurements.
PROD_PDF_QUALITROL_CORE_PACKAGE | Qualitrol Core Package | PF_DGA | MET_SENSOR_TYPE | Sensor mounting |  |  | Single Valve mount, directly immersed sensor, no membrane | text |  |  | Preparation/Qualitrol Product/Software_Solutions/Core_Package_02229adb.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Single Valve mount... No Membrane - directly immersed sensor
PROD_PDF_QUALITROL_CORE_PACKAGE | Qualitrol Core Package | PF_DGA | MET_PROTOCOL | Communication protocols |  |  | IEC-61850, ModBUS, DNP3.0 | text |  |  | Preparation/Qualitrol Product/Software_Solutions/Core_Package_02229adb.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Suports IEC-61850, ModBUS, DNP3.0
PROD_PDF_QUALITROL_CORE_PACKAGE | Qualitrol Core Package | PF_DGA | MET_ENCLOSURE_RATING | Chassis and mounting |  |  | Multiple chassis sizes and mounting options | text |  |  | Preparation/Qualitrol Product/Software_Solutions/Core_Package_02229adb.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Multiple chassis sizes and mounting options to suit any application
PROD_PDF_QUALITROL_CORE_PACKAGE | Qualitrol Core Package | PF_DGA | MET_LICENSE_SCOPE | APM software |  |  | On-premise enterprise APM, scalable platform | text |  |  | Preparation/Qualitrol Product/Software_Solutions/Core_Package_02229adb.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Homegrown Asset Performance Management (APM) software that is an on-premise solution
PROD_PDF_PDTECH_DRA_3 | PDTech DRA-3 | PF_GEN_PD | MET_POWER_SUPPLY | Input Voltage | 90 | 240 | Universal 90 to 240 VAC | VAC |  |  | Preparation/Qualitrol Product/Software_Solutions/DRA3_Software_3041882e.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Input Voltage Universal 90 to 240 VAC
PROD_PDF_PDTECH_DRA_3 | PDTech DRA-3 | PF_GEN_PD | MET_NETWORK | Computer interface |  |  | USB (5 m USB cable) | text |  |  | Preparation/Qualitrol Product/Software_Solutions/DRA3_Software_3041882e.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: A 5 m USB Cable
PROD_PF_SOFTWARE_03 | iQ+ Master Station | PF_SOFTWARE | MET_PROTOCOL | Data export format |  |  | COMTRADE / PQDIF | text |  |  | Preparation/Qualitrol Product/Software_Solutions/IQ+_68057b47.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Manual or scheduled automatic data export to COMTRADE / PQDIF
PROD_PF_SOFTWARE_03 | iQ+ Master Station | PF_SOFTWARE | MET_NETWORK | Network interface |  |  | TCP/IP over Substation LAN | text |  |  | Preparation/Qualitrol Product/Software_Solutions/IQ+_68057b47.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: TCP/IP TCP/IP TCP/IP TCP/IP ... SUBSTATION LAN
PROD_PF_SOFTWARE_03 | iQ+ Master Station | PF_SOFTWARE | MET_LICENSE_SCOPE | Deployment scope |  |  | Single user/unit to complete fleet wide deployment | text |  |  | Preparation/Qualitrol Product/Software_Solutions/IQ+_68057b47.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: iQ+ can be installed as single user / unit to multiple users
PROD_PF_SOFTWARE_03 | iQ+ Master Station | PF_SOFTWARE | MET_FEEDER_COUNT | Distance to fault multi-ended circuits |  | 6 | up to 6 | count |  |  | Preparation/Qualitrol Product/Software_Solutions/IQ+_68057b47.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Distance to fault for multi-ended circuits (up to 6)
PROD_PF_SOFTWARE_03 | iQ+ Master Station | PF_SOFTWARE | MET_DFR_FUNCTIONS | Supported devices |  |  | DFR (IDM+, IDM-E, BEN 6000), TWS FL, PQ monitors | text |  |  | Preparation/Qualitrol Product/Software_Solutions/IQ+_68057b47.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Digital fault recorders (DFR): IDM+, IDM-E, BEN 6000
PROD_PF_SOFTWARE_03 | iQ+ Master Station | PF_SOFTWARE | MET_PQ_CLASS | Power quality standards templates |  |  | EN 50160 / IEC 61000-3-6/7 | text |  |  | Preparation/Qualitrol Product/Software_Solutions/IQ+_68057b47.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: built in EN 50160 / IEC 61000-3-6/7
PROD_PDF_QUALITROL_SMARTSUB | Qualitrol SmartSUB | PF_SOFTWARE | MET_PROTOCOL | Communication Protocols |  |  | IEC-61850, IEC-61870, DNP3.0, MODBUS | text |  |  | Preparation/Qualitrol Product/Software_Solutions/SmartSUB_342941d3.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: protocols including IEC-61850, IEC-61870, DNP3.0, and MODBUS
PROD_PDF_QUALITROL_SMARTSUB | Qualitrol SmartSUB | PF_SOFTWARE | MET_ASSET_TYPE | Supported Asset Types |  |  | transformer, breaker, gas insulated switchgear, generator | text |  |  | Preparation/Qualitrol Product/Software_Solutions/SmartSUB_342941d3.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: such as transformer, breaker, gas insulated switchgear, generator
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_DGA_GAS_COUNT | Fault gases measured | 8 |  | 8 critical fault gases plus nitrogen | count |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: measurements of the 8 critical fault gases plus nitrogen
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_DGA_GAS_SPECIES | Gas species |  |  | H2, O2, CO, CH4, CO2, C2H4, C2H6, C2H2, N2 | text |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Hydrogen (H2) Oxygen (O2) Carbon Monoxide (CO) Methane (CH4)
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_DGA_GAS_SPECIES | Hydrogen range | 3 | 3000 | 3-3,000 ppm | ppm |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 3-3,000 ppm
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_DGA_GAS_SPECIES | Oxygen range | 30 | 25000 | 30-25,000 ppm | ppm |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 30-25,000 ppm
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_DGA_GAS_SPECIES | Carbon Monoxide range | 5 | 7000 | 5-7,000 ppm | ppm |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 5-7,000 ppm
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_DGA_GAS_SPECIES | Methane range | 5 | 10000 | 5-10,000 ppm | ppm |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 5-10,000 ppm
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_DGA_GAS_SPECIES | Carbon Dioxide range | 5 | 30000 | 5-30,000 ppm | ppm |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 5-30,000 ppm
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_DGA_GAS_SPECIES | Ethylene range | 3 | 5000 | 3-5,000 ppm | ppm |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 3-5,000 ppm
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_DGA_GAS_SPECIES | Ethane range | 5 | 5000 | 5-5,000 ppm | ppm |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 5-5,000 ppm
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_DGA_GAS_SPECIES | Acetylene range | 1 | 3000 | 1-3,000 ppm | ppm |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 1-3,000 ppm
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_DGA_GAS_SPECIES | Nitrogen range | 5000 | 100000 | 5,000-100,000 ppm | ppm |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 5,000-100,000 ppm
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_MOISTURE_OIL | Moisture-in-Oil range | 0 | 100 | 0-100% RS | %RS |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 0-100% RS
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_OIL_TEMPERATURE | Oil Temperature range | -40 | 120 | -40°C to +120°C | °C |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: -40°C to +120°C
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_SENSOR_TYPE | External sensor inputs |  |  | Three (3) analog 4 to 20 mA inputs, ambient temperature sensor included | text |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Three (3) analog 4 to 20 mA inputs, ambient temperature sensor included
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_CONTACT_TYPE | Alarm relays |  |  | Two individually programmable relays, normally open or normally closed | text |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Two individually programmable relays
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_ALARM_THRESHOLD | Supported alarms |  |  | Gas Caution & Alarm for Level, Rate-of-Change, Power and/or Service Event | varies |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Gas Caution & Alarm for Level (ppm), Rate-of-Change (ppm/day)
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_PROTOCOL | Supported protocols |  |  | TCP/IP, DNP3, Modbus RTU, ASCII, OPC, IEC 61850 | text |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: TCP/IP, DNP3, Modbus RTU, ASCII, OPC and IEC 61850
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_NETWORK | Communication interfaces |  |  | RS-232, RS-485, Ethernet Fiber (100Base-FX), POTS modem; optional cellular, Ethernet Copper | text |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: RS-232, RS-485, Ethernet Fiber (100Base-FX), V.92 Internal POTS modem
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_POWER_SUPPLY | Input power |  |  | 110-240 Vac or 125-250 Vdc, 50/60 Hz, 6 A max | V AC/DC |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: 110-240 Vac or 125-250 Vdc
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_AMBIENT_TEMP | Operating temperature | -50 | 55 | -50°C to +55°C | °C |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Operating Temperature -50°C to +55°C
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_HUMIDITY | Operating humidity | 5 | 95 | 5% to 95% RH, non-condensing | %RH |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: 5% to 95% RH, non-condensing
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_ENCLOSURE_RATING | Enclosure rating |  |  | NEMA 4X, IP66 | text |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Enclosure Rating NEMA 4X, IP66
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_SAMPLING_RATE | Oil sampling / gas analysis interval | 2 | 12 | Continuous oil sampling; analysis 2-12 hours (default 4) | hours |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: user-selectable from 2 hours to 12 hours (Default: 4 hours)
PROD_PDF_IRIS_POWER_DCR_60_2 | Iris Power DCR 60-2 | PF_GEN_PD | MET_POWER_SUPPLY | Power Supply | 85 | 264 | 85-264 V AC, 2A, 50/60 Hz | V AC |  |  | Preparation/Qualitrol Product/The_Power_Grid/DCR_60_4ae9ab6d.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Power Supply 85-264 V AC, 2A, 50/60 Hz
PROD_PDF_IRIS_POWER_DCR_60_2 | Iris Power DCR 60-2 | PF_GEN_PD | MET_NETWORK | PC Interface |  |  | USB interface; Windows 7 | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/DCR_60_4ae9ab6d.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: PC USB interface; Windows 7
PROD_PDF_IRIS_POWER_DCR_60_2 | Iris Power DCR 60-2 | PF_GEN_PD | MET_AMBIENT_TEMP | Operating Temperature | 0 | 40 | 0° to +40°C | °C |  |  | Preparation/Qualitrol Product/The_Power_Grid/DCR_60_4ae9ab6d.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Operating Temperature 0° to +40°C (+32° to +104°F)
PROD_PDF_IRIS_POWER_DCR_60_2 | Iris Power DCR 60-2 | PF_GEN_PD | MET_PROTOCOL | Standards Compliance |  |  | IEEE Standard 95-2002 | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/DCR_60_4ae9ab6d.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Compliant with IEEE Standard 95 -2002
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_ANALOG_CHANNELS | Analog channels (IDM+ 9) |  |  | 9 analog and 32 digital channels (3U) | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 9 analog and 32 digital channels (3U)
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_ANALOG_CHANNELS | Analog channels (IDM+ 18) |  |  | 18 analog and 64 digital channels (6U) | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 18 analog and 64 digital channels (6U)
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_ANALOG_CHANNELS | Analog channels (IDM+ 36) |  |  | 36 analog and 128 digital channels (6U) | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 36 analog and 128 digital channels (6U)
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_SAMPLING_RATE | Sampling rate |  |  | 512 samples per cycle (30.7 kHz at 60 Hz, 25.6 kHz at 50 Hz) | samples/cycle |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Sampling rate of 512 samples per cycle (30.7 kHz at 60 Hz
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_SAMPLING_RATE | DFR sample rate range | 1.9 | 30.7 | 30.7 kHz to 1.9 kHz on 60 Hz systems | kHz |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: set DFR sample rates from 30.7 kHz to 1.9 kHz
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_DFR_FUNCTIONS | Recorder functions |  |  | DFR, DDR, PMU, TWS FL, Class A PQ | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: DFR, DDR, PMU, TWS FL and Class A PQ in ONE device
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_LINE_COUNT | Lines monitored | 1 | 2 | Monitor 1 or 2 lines | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Monitor 1 or 2 lines – depending on unit
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_TIME_SYNC | Time synchronization |  |  | GPS, IRIG-B with 1pps or IRIG-J, NTP | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: synchronized by GPS module or IRIG-B with 1pps or IRIG-J options
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_GPS_SYNC_ACCURACY | GPS time accuracy |  |  | 100 ns | ns |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: achieve a time accuracy of 100 ns
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_PQ_CLASS | Power quality class |  |  | Class A per IEC 61000-4-30 | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: fully certified as meeting the IEC standard to Class A accuracy
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_HARMONICS | Harmonics measurement | 1 | 50 | Voltage and current harmonics 1st-50th order (IEC 61000-4-7) | order |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Voltage and current harmonics 1st – 50th order
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_FLICKER | Flicker |  |  | Short and long term flicker Pst and Plt per IEC 61000-4-15 | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Short and long term flicker – Pst and Plt according IEC 61000-4-15
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_SAG_SWELL | Sag/swell recording |  |  | Voltage dips (sags), swells and interruptions logged | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: voltage dips (sags), swells and interruptions are logged
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_REPORTING_RATE | PMU compliance |  |  | IEEE C37.118-2005 compliant PMU | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: phasor measurement unit fully compliant with the IEEE C37.118-2005 standard
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_PROTOCOL | Communication protocols |  |  | IEC 61850, IEC 60870-5, DNP, Modbus | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: protocols including IEC 61850, IEC 60870-5, DNP and Modbus
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_NETWORK | Network interface |  |  | Ethernet (RJ45 or fibre), modem or serial port | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Communications is via ethernet (RJ45 or fibre), modem or serial port
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_ENCLOSURE_RATING | Enclosure |  |  | 3U or 6U 19 inch rack mountable enclosure | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 19 inch rack mountable enclosure
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_POWER_SUPPLY | Power supply option |  |  | Uninterruptable power supply option on 3U version | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Uninterruptable power supply option available on 3U version
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | MET_PQ_CLASS | Power quality class |  |  | IEC 61000-4-30 Class A (Edition 2.0) | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/Informa_PQ_17eb70e4.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: Power quality monitoring - IEC 61000-4-30 Class A
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | MET_ANALOG_CHANNELS | Analog channels | 9 | 36 | 9/18/27/36 configurable analog channels for 6U device | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/Informa_PQ_17eb70e4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 9/18/27/36 configurable analog channels for INFORMA PMD-A 6U device
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | MET_SAMPLING_RATE | Sampling rate |  |  | 25.6 kHz at 50 Hz, 30.72 kHz at 60 Hz | Hz |  |  | Preparation/Qualitrol Product/The_Power_Grid/Informa_PQ_17eb70e4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Sampling rate 25.6 kHz at 50 Hz, 30.72 kHz at 60 Hz
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | MET_SAMPLING_RATE | Fault record sampling |  |  | 512 samples per cycle | samples/cycle |  |  | Preparation/Qualitrol Product/The_Power_Grid/Informa_PQ_17eb70e4.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Fault records (512 samples per cycle) combine analog and digital events
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | MET_SAMPLING_RATE | Transient recording sampling rate |  |  | 20 MHz, 10 MHz, 5 MHz, 2.5 MHz, 1.25 MHz | Hz |  |  | Preparation/Qualitrol Product/The_Power_Grid/Informa_PQ_17eb70e4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Sampling rates (user configurable): 20 MHz, 10 MHz, 5 MHz
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | MET_SAG_SWELL | Sag/swell triggered recordings |  |  | Triggered recordings for sags/dips, swells, interruptions | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/Informa_PQ_17eb70e4.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Triggered recordings for sags / dips, swells, interruptions, rapid voltage changes
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | MET_DFR_FUNCTIONS | Digital fault recording |  |  | Full function digital fault recording; variable record up to 30 seconds | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/Informa_PQ_17eb70e4.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Variable record length up to 30 seconds
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | MET_TIME_SYNC | Time synchronization / clock sync |  |  | Clock sync (LED status indicator) | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/Informa_PQ_17eb70e4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 9 LEDs - healthy, communication, clock sync, battery
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | MET_POWER_SUPPLY | Power supply input range |  |  | Type 1: 90-264 VAC (88-300 VDC); Type 2: 36-72 VDC; Type 3: 18-36 VDC | V AC/DC |  |  | Preparation/Qualitrol Product/The_Power_Grid/Informa_PQ_17eb70e4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Type 1: 90 - 264 VAC (88-300 VDC), 47 -63 Hz
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | MET_NETWORK | Network / data interface |  |  | Ethernet, RS232, USB | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/Informa_PQ_17eb70e4.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: Tested on power line, RS232 -1, Ethernet port 1
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | MET_VOLTAGE_CHANNELS | Nominal AC voltage full scale |  |  | 63.5(140), 120(270), 240(480), 440(800) VAC | V |  |  | Preparation/Qualitrol Product/The_Power_Grid/Informa_PQ_17eb70e4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Nominal (full scale) in VAC: 63.5 (140), 120 (270), 240 (480), 440 (800)
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | MET_HARMONICS | Harmonic reporting |  |  | Harmonic reports in 3 second intervals | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/Informa_PQ_17eb70e4.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: harmonic reports in 3 second intervals
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | MET_ALARM_THRESHOLD | User-defined thresholds |  |  | Standard or user-defined thresholds (e.g. dips -10% changeable to -15%) | varies |  |  | Preparation/Qualitrol Product/The_Power_Grid/Informa_PQ_17eb70e4.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: dips defined at -10 % in EN 50160 can be changed to user thresholds of -15 %
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | MET_ENCLOSURE_RATING | Device form factor |  |  | 3U and 6U device | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/Informa_PQ_17eb70e4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 9 configurable analog channels for INFORMA PMD-A 3U device
PROD_PF_TWS_04 | TWS FL-8 | PF_TWS | MET_LINE_COUNT | Line ends monitored | 2 | 8 | 2, 4, 6 or 8 lines | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: 2 line modules expandable to 8 in steps of 2
PROD_PF_TWS_04 | TWS FL-8 | PF_TWS | MET_DFR_FUNCTIONS | Fault location accuracy |  |  | ±60 meters [±195 feet] | m |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Best accuracy to ±60 meters [±195 feet] independent of impedance methods
PROD_PF_TWS_04 | TWS FL-8 | PF_TWS | MET_ANALOG_CHANNELS | Channels per line module |  |  | 3 (one per phase) from external linear couplers - 12 bit ADC | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: 3 (one per phase) from external linear couplers - 12 bit ADC
PROD_PF_TWS_04 | TWS FL-8 | PF_TWS | MET_SENSOR_TYPE | Transducer type |  |  | Split-core linear couplers around protection CT secondary wiring | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Split-core linear couplers are placed around the secondary wiring
PROD_PF_TWS_04 | TWS FL-8 | PF_TWS | MET_SAMPLING_RATE | Sample rate |  |  | 20 MHz, 10 MHz, 5 MHz, 2.5 MHz or 1.25 MHz | Hz |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: 20 MHz, 10 MHz, 5 MHz, 2.5 MHz or 1.25 MHz
PROD_PF_TWS_04 | TWS FL-8 | PF_TWS | MET_TIME_SYNC | Time synchronization |  |  | Internal GPS module (master) or NTP over LAN + 1 pps (slave); IRIG-B out | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: Synchronized by internal GPS module (master) or via NTP
PROD_PF_TWS_04 | TWS FL-8 | PF_TWS | MET_GPS_SYNC_ACCURACY | Clock accuracy |  |  | Master 100 ns. Slave 1 microsecond | ns |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: Master 100 ns. Slave 1 microsecond
PROD_PF_TWS_04 | TWS FL-8 | PF_TWS | MET_POWER_SUPPLY | Power supply voltage range | 88 | 300 | 88 - 300 VDC / VAC, 42.5 to 67.5 Hz (optional 36 - 72 VDC) | V AC/DC |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: 88 - 300 VDC / VAC, 42.5 to 67.5 Hz (optional 36 - 72 VDC)
PROD_PF_TWS_04 | TWS FL-8 | PF_TWS | MET_CONTACT_TYPE | Alarm relays |  |  | 1 NC system healthy; 3 NO lost lock/trigger/high priority/buffer full | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: 1 (normally closed) for system healthy
PROD_PF_TWS_04 | TWS FL-8 | PF_TWS | MET_PROTOCOL | Line trip detection protocol |  |  | Digital input change of state or 61850 GOOSE message | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: digital input or a 61850 GOOSE message
PROD_PF_TWS_04 | TWS FL-8 | PF_TWS | MET_NETWORK | Ethernet ports |  |  | 2 x 100 Mbits RJ45 (rear optional fiber) | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: 2 x 100 Mbits - one RJ45 for local connection
PROD_PF_TWS_04 | TWS FL-8 | PF_TWS | MET_AMBIENT_TEMP | Operating temperature | -5 | 50 | Operating: -5 to +50º C | °C |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: Operating: -5 to +50º C [23 to 122º F]
PROD_PF_TWS_04 | TWS FL-8 | PF_TWS | MET_HUMIDITY | Humidity | 0 | 95 | 0 to 95% non-condensing | %RH |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: 0 to 95% non-condensing
PROD_PF_TWS_04 | TWS FL-8 | PF_TWS | MET_ENCLOSURE_RATING | Enclosure rating |  |  | IP 41, 19” rack-mountable, 3U device | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: IP 41, 19” rack-mountable
PROD_PF_TWS_05 | TWS FL-1 | PF_TWS | MET_LINE_COUNT | Line ends monitored |  |  | 1 line (fixed format with one line module) | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: Fixed format with one line module
PROD_PF_TWS_05 | TWS FL-1 | PF_TWS | MET_DFR_FUNCTIONS | Fault location accuracy |  |  | ±60 meters [±195 feet] | m |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Best accuracy to ±195 feet [±60 meters] independent of impedance methods
PROD_PF_TWS_05 | TWS FL-1 | PF_TWS | MET_ANALOG_CHANNELS | Channels per line module |  |  | 3 (one per phase) from external linear couplers - 12 bit ADC | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: 3 (one per phase) from external linear couplers - 12 bit ADC
PROD_PF_TWS_05 | TWS FL-1 | PF_TWS | MET_SENSOR_TYPE | Transducer type |  |  | Split-core linear couplers around protection CT secondary wiring | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Split-core linear couplers are placed around the secondary wiring
PROD_PF_TWS_05 | TWS FL-1 | PF_TWS | MET_SAMPLING_RATE | Sample rate |  |  | 20 MHz, 10 MHz, 5 MHz, 2.5 MHz or 1.25 MHz | Hz |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: 20 MHz, 10 MHz, 5 MHz, 2.5 MHz or 1.25 MHz
PROD_PF_TWS_05 | TWS FL-1 | PF_TWS | MET_GPS_SYNC_ACCURACY | Clock accuracy |  |  | Master 100 ns. Slave 1 microsecond | ns |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: Master 100 ns. Slave 1 microsecond
PROD_PF_TWS_05 | TWS FL-1 | PF_TWS | MET_POWER_SUPPLY | Power supply voltage range | 88 | 300 | 88 - 300 VDC / VAC, 42.5 to 67.5 Hz (optional 36 - 72 VDC) | V AC/DC |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: 88 - 300 VDC / VAC, 42.5 to 67.5 Hz
PROD_PF_TWS_05 | TWS FL-1 | PF_TWS | MET_ENCLOSURE_RATING | Enclosure rating |  |  | IP 41, 19” rack-mountable, 2U device | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: 2U device - H x W x D: 90 mm
PROD_PF_TWS_05 | TWS FL-1 | PF_TWS | MET_AMBIENT_TEMP | Operating temperature | -5 | 50 | Operating: -5 to +50º C | °C |  |  | Preparation/Qualitrol Product/The_Power_Grid/TWS_FL_1016871a.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: Operating: -5 to +50º C [23 to 122º F]
PROD_PDF_QUALITROL_015_VERTICAL_OIL_LEVEL_INDICATOR | Qualitrol 015 Vertical Oil Level Indicator | PF_AUX_SENSOR | MET_OIL_TEMPERATURE | Oil temperature | 0 | 120 | 32°F to 248°F (0°C to 120°C) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/015_Vertical_Oil_Level_Indicator_fb43241e.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Oil temperature 32°F to 248°F (0°C to 120°C)
PROD_PDF_QUALITROL_015_VERTICAL_OIL_LEVEL_INDICATOR | Qualitrol 015 Vertical Oil Level Indicator | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Ambient temperature | -40 | 85 | -40°F to 185°F (-40°C to 85°C) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/015_Vertical_Oil_Level_Indicator_fb43241e.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Ambient temperature -40°F to 185°F (-40°C to 85°C)
PROD_PDF_QUALITROL_015_VERTICAL_OIL_LEVEL_INDICATOR | Qualitrol 015 Vertical Oil Level Indicator | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Enclosure |  |  | Vented, IP55 (NEMA 3R) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/015_Vertical_Oil_Level_Indicator_fb43241e.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Vented, meets the requirements of IP55 (NEMA 3R)
PROD_PDF_QUALITROL_015_VERTICAL_OIL_LEVEL_INDICATOR | Qualitrol 015 Vertical Oil Level Indicator | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch ratings |  |  | SPDT 3A @ 250 VAC, UL listed and CSA approved | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/015_Vertical_Oil_Level_Indicator_fb43241e.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Switch ratings SPDT 3A @ 250 VAC, UL listed
PROD_PDF_QUALITROL_029_VERTICAL_OIL_LEVEL_INDICATOR | Qualitrol 029 Vertical Oil Level Indicator | PF_AUX_SENSOR | MET_SENSOR_TYPE | Float Mechanism |  |  | Geared float mechanism | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/029_Subway_Oil_Level_Indicator_8f7dd70b.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Float mechanism Geared
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_SENSOR_TYPE | Float mechanism (032/042/045) |  |  | Gear (042 and 045 series) or lever (032 series) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Gear (042 and 045 series) or lever (032 series)
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_SENSOR_TYPE | Float mechanism (44712/34725) |  |  | Gear (34725) or lever (44712) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Gear (34725) or lever (44712)
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_CONTACT_TYPE | Number of switches (032/042/045) |  | 3 | Up to 3 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Number of switches Up to 3
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_CONTACT_TYPE | Number of switches (44712/34725) |  | 4 | 4 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Number of switches 4
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type (032/042/045) |  |  | SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Switch type SPDT
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type (44712/34725) |  |  | SPST or SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch type SPST or SPDT
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_PROTOCOL | SCADA output signal (032/042/045) |  |  | 4-20mA or 0-1mA (Only with 039 Remote Enclosure) | mA |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 4 - 20mA or 0 - 1mA (Only with 039 Remote Enclosure)
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_PROTOCOL | SCADA output signal (44712/34725) |  |  | 4-20 mA | mA |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Output signal 4 - 20 mA
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_POWER_SUPPLY | Supply voltage (032/042/045) |  |  | 24 VDC nominal (120 or 240 VAC on 039 series) | V |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 24 VDC nominal (120 or 240 VAC on 039 series)
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_POWER_SUPPLY | Supply voltage (44712/34725) |  |  | 24 VDC nominal | V |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Supply voltage 24 VDC nominal
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Hazardous location rating |  |  | UL listed for class 1 div 2 (045 models) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 045 models are designed for hazerdous locations and are UL listed for class 1 div 2
PROD_PDF_QUALITROL_035_LIQUID_LEVEL_CONTROL_GAUGE | QUALITROL 035 Liquid Level Control Gauge | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type |  |  | SPDT (up to two independent switch contacts) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/035_Flange_Mounted_Liquid_Level_Gauge_3a00eded.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch type SPDT
PROD_PDF_QUALITROL_035_LIQUID_LEVEL_CONTROL_GAUGE | QUALITROL 035 Liquid Level Control Gauge | PF_AUX_SENSOR | MET_ALARM_THRESHOLD | Alarm control |  |  | Low level and high level alarm control via integrated switches | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/035_Flange_Mounted_Liquid_Level_Gauge_3a00eded.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Low level and high level alarm control is made possible with integrated switches
PROD_PDF_QUALITROL_038_GAS_ACCUMULATION_INDICATOR | QUALITROL 038 Gas Accumulation Indicator | PF_AUX_SENSOR | MET_ALARM_THRESHOLD | Alarm actuation gas volume |  |  | greater than 200cc of oil displacement | cc |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/038_Gas_Accumulation_Indicator_a3362790.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: actuates when the accumulated gas displaces greater than 200cc of oil
PROD_PDF_QUALITROL_038_GAS_ACCUMULATION_INDICATOR | QUALITROL 038 Gas Accumulation Indicator | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Case rating |  |  | Sealed or vented, meets IP54 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/038_Gas_Accumulation_Indicator_a3362790.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Case Sealed or vented, meets IP54
PROD_PDF_QUALITROL_038_GAS_ACCUMULATION_INDICATOR | QUALITROL 038 Gas Accumulation Indicator | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Standard operating temperatures | -40 | 80 | -40 to +80ºC | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/038_Gas_Accumulation_Indicator_a3362790.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Std. operating -40 to +176ºF (-40 to +80ºC.)
PROD_PDF_QUALITROL_038_GAS_ACCUMULATION_INDICATOR | QUALITROL 038 Gas Accumulation Indicator | PF_AUX_SENSOR | MET_HUMIDITY | Ambient humidity | 35 | 100 | 35% to 100% | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/038_Gas_Accumulation_Indicator_a3362790.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient humidity 35% to 100%
PROD_PDF_QUALITROL_038_GAS_ACCUMULATION_INDICATOR | QUALITROL 038 Gas Accumulation Indicator | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type |  |  | Snap action - SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/038_Gas_Accumulation_Indicator_a3362790.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch type Snap action - SPDT
PROD_PDF_QUALITROL_032_042_045 | QUALITROL 032/042/045 | PF_AUX_SENSOR | MET_POWER_SUPPLY | Supply voltage |  |  | 24 VDC nominal (120 or 240 VAC on 039 series) | V |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 24 VDC nominal (120 or 240 VAC on 039 series)
PROD_PDF_QUALITROL_AKM_44712_34725 | QUALITROL AKM 44712/34725 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type |  |  | SPST or SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch type SPST or SPDT
PROD_PDF_QUALITROL_AKM_44712_34725 | QUALITROL AKM 44712/34725 | PF_AUX_SENSOR | MET_POWER_SUPPLY | Supply voltage |  |  | 24 VDC nominal | V |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Supply voltage 24 VDC nominal
PROD_PDF_QUALITROL_049 | Qualitrol 049 | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Enclosure rating |  |  | IP54 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/049_Vertical_Oil_Level_Indicator_b0a06108.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Vented enclosure meets IP54 requirements
PROD_PDF_QUALITROL_049 | Qualitrol 049 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Ambient operating temperature | -40 | 55 | -40°F to 131°F (-40°C to 55°C) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/049_Vertical_Oil_Level_Indicator_b0a06108.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Ambient operating -40°F to 131°F (-40°C to 55°C)
PROD_PDF_QUALITROL_049 | Qualitrol 049 | PF_AUX_SENSOR | MET_OIL_TEMPERATURE | Oil temperature range | 0 | 100 | 32°F to 212°F (0°C to 100°C) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/049_Vertical_Oil_Level_Indicator_b0a06108.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Oil temperature range 32°F to 212°F (0°C to 100°C)
PROD_PDF_QUALITROL_049 | Qualitrol 049 | PF_AUX_SENSOR | MET_HUMIDITY | Ambient humidity | 35 | 100 | 35% to 100% | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/049_Vertical_Oil_Level_Indicator_b0a06108.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Ambient humidity 35% to 100%
PROD_PDF_QUALITROL_049 | Qualitrol 049 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch |  |  | One SPDT snap-action switch (UL listed and CSA approved) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/049_Vertical_Oil_Level_Indicator_b0a06108.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: One SPDT snap-action switch (UL listed and CSA approved)
PROD_PDF_QUALITROL_049 | Qualitrol 049 | PF_AUX_SENSOR | MET_POWER_SUPPLY | Switch rating |  |  | 5A @ 125/250 VAC | V AC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/049_Vertical_Oil_Level_Indicator_b0a06108.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Switch rating 5A @ 125/250 VAC
PROD_PDF_QUALITROL_050 | Qualitrol 050 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Ambient operating temperature | -50 | 82 | -58 to 180° F (-50 to 82 C°) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/050_PressureVacuum_Gauge_and_Bleeders_940edfee.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Ambient operating temperature -58 to 180° F (-50 to 82 C°)
PROD_PDF_QUALITROL_050 | Qualitrol 050 | PF_AUX_SENSOR | MET_VIBRATION | Vibration resistance |  |  | Not affected at 60 Hz or whole multiples thereof | Hz |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/050_PressureVacuum_Gauge_and_Bleeders_940edfee.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Not affected when subjected to 60 Hz
PROD_PDF_QUALITROL_070_SERIES_PRESSURE_VACUUM_BLEEDER | QUALITROL 070 Series Pressure-Vacuum Bleeder | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Ambient operating temperatures | -40 | 70 | -40°F to 158°F (-40ºC to 70ºC) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/070_PressureVacuum_Gauge_and_Bleeders_36edcc50.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient operating -40°F to 158°F (-40ºC to 70ºC)
PROD_PDF_QUALITROL_351_SERIES_PRESSURE_VACUUM_BLEEDER | QUALITROL 351 Series Pressure-Vacuum Bleeder | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Ambient operating temperatures | -40 | 70 | -40°F to 158°F (-40ºC to 70ºC) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/070_PressureVacuum_Gauge_and_Bleeders_36edcc50.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient operating -40°F to 158°F (-40ºC to 70ºC)
PROD_PDF_QUALITROL_092_FLOW_INDICATORS | QUALITROL 092 Flow Indicators | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type |  |  | Snap action, SPST or SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/092_Flow_Gauge_13c5e971.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch type Snap action, SPST or SPDT
PROD_PDF_QUALITROL_092_FLOW_INDICATORS | QUALITROL 092 Flow Indicators | PF_AUX_SENSOR | MET_SENSOR_COUNT | Number of switches |  | 2 | Up to 2 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/092_Flow_Gauge_13c5e971.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Number of switches Up to 2
PROD_PDF_QUALITROL_092_FLOW_INDICATORS | QUALITROL 092 Flow Indicators | PF_AUX_SENSOR | MET_POWER_SUPPLY | Switch rating (AC) |  |  | 10 amp @ 125, 250 & 480 VAC | V AC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/092_Flow_Gauge_13c5e971.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 10 amp @ 125, 250 & 480 VAC
PROD_PDF_QUALITROL_092_FLOW_INDICATORS | QUALITROL 092 Flow Indicators | PF_AUX_SENSOR | MET_POWER_SUPPLY | Switch rating (DC) |  |  | ½A@125VDC, ¼A@250VDC, 1½A@48VDC | V DC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/092_Flow_Gauge_13c5e971.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: ½ Amp @ 125 VDC - resistive
PROD_PDF_QUALITROL_092_FLOW_INDICATORS | QUALITROL 092 Flow Indicators | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | IP rating (sealed cases) |  |  | Meets IP66 requirements | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/092_Flow_Gauge_13c5e971.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: IP ratings (sealed cases) Meets IP66 requirements
PROD_PDF_QUALITROL_092_FLOW_INDICATORS | QUALITROL 092 Flow Indicators | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | IP rating (vented cases) |  |  | Meets IP54 requirements | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/092_Flow_Gauge_13c5e971.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: IP ratings (vented cases) Meets IP54 requirments
PROD_PDF_QUALITROL_092_FLOW_INDICATORS | QUALITROL 092 Flow Indicators | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Ambient operating temperatures | -34 | 60 | -30 to 140ºF (-34 to 60ºC) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/092_Flow_Gauge_13c5e971.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient operating temperatures -30 to 140ºF (-34 to 60ºC)
PROD_PDF_QUALITROL_092_FLOW_INDICATORS | QUALITROL 092 Flow Indicators | PF_AUX_SENSOR | MET_PROTOCOL | Electrical connections |  |  | QUALITROL, Military, ANSI, cable, flying leads | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/092_Flow_Gauge_13c5e971.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: QUALITROL, Military, ANSI, permamently attached cable, flying leads
PROD_PDF_QUALITROL_104_TR6000_REMOTE_MOUNT_THERMOMETERS | QUALITROL 104/TR6000 Remote Mount Thermometers | PF_TR_TEMP | MET_OIL_TEMPERATURE | Standard dial ranges | -20 | 220 | 1-120, 0-160, 0-180, -20-180, 0-200, 0-220, -20 to 160 | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/104TR6000_Remote_Temperature_Indicator_5d6da65e.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Standard dial ranges 1-120, 0-160, 0-180, -20-180, 0-200, 0-220
PROD_PDF_QUALITROL_104_TR6000_REMOTE_MOUNT_THERMOMETERS | QUALITROL 104/TR6000 Remote Mount Thermometers | PF_TR_TEMP | MET_PROTOCOL | SCADA analog output |  |  | 0-1 mA and 4-20 mA | mA |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/104TR6000_Remote_Temperature_Indicator_5d6da65e.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: SCADA outputs (0-1 mA or 4-20 mA) are available
PROD_PDF_QUALITROL_104_TR6000_REMOTE_MOUNT_THERMOMETERS | QUALITROL 104/TR6000 Remote Mount Thermometers | PF_TR_TEMP | MET_AMBIENT_TEMP | Ambient operating temperature | -40 | 60 | -40 to 140°F (-40 to +60ºC) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/104TR6000_Remote_Temperature_Indicator_5d6da65e.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Ambient operating temperature -40 to 140°F (-40 to +60ºC)
PROD_PDF_QUALITROL_104_TR6000_REMOTE_MOUNT_THERMOMETERS | QUALITROL 104/TR6000 Remote Mount Thermometers | PF_TR_TEMP | MET_AMBIENT_TEMP | Storage temperature | -50 | 80 | -45 to 176°F (-50 to +80ºC) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/104TR6000_Remote_Temperature_Indicator_5d6da65e.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Storage temperature -45 to 176°F (-50 to +80ºC)
PROD_PDF_QUALITROL_104_TR6000_REMOTE_MOUNT_THERMOMETERS | QUALITROL 104/TR6000 Remote Mount Thermometers | PF_TR_TEMP | MET_HUMIDITY | Relative humidity |  | 90 | 90% (non-condensing) | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/104TR6000_Remote_Temperature_Indicator_5d6da65e.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Relative humidity 90% (non-condensing)
PROD_PDF_QUALITROL_104_TR6000_REMOTE_MOUNT_THERMOMETERS | QUALITROL 104/TR6000 Remote Mount Thermometers | PF_TR_TEMP | MET_CONTACT_TYPE | Standard switch type |  |  | Low-force, single-pole-double-throw (SPDT) changeover switch | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/104TR6000_Remote_Temperature_Indicator_5d6da65e.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: single-pole-double-throw (SPDT) changeover switch
PROD_PDF_QUALITROL_104_TR6000_REMOTE_MOUNT_THERMOMETERS | QUALITROL 104/TR6000 Remote Mount Thermometers | PF_TR_TEMP | MET_SENSOR_COUNT | Number of switches |  | 4 | Up to 4 user adjustable | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/104TR6000_Remote_Temperature_Indicator_5d6da65e.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Number of switches Up to 4 user adjustable
PROD_PDF_QUALITROL_104_TR6000_REMOTE_MOUNT_THERMOMETERS | QUALITROL 104/TR6000 Remote Mount Thermometers | PF_TR_TEMP | MET_ENCLOSURE_RATING | Housing material |  |  | Die-cast aluminum with thermosetting powder coat finish | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/104TR6000_Remote_Temperature_Indicator_5d6da65e.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Housing Die-cast aluminum with thermosetting powder coat finish
PROD_PDF_QUALITROL_105_REMOTE_MOUNT_THERMOMETER | QUALITROL 105 Remote Mount Thermometer | PF_TR_TEMP | MET_OIL_TEMPERATURE | Standard dial ranges | 0 | 250 | 0-120, 0-160, 0-180, 20-180, 0-200, 0-220, 0-250 ºC | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/105_Remote_Mount_Thermometer_b568f343.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Standard dial ranges 0-120ºC, 0-160ºC, 0-180ºC, 20-180ºC, 0-200ºC, 0-220ºC, 0-250ºC
PROD_PDF_QUALITROL_105_REMOTE_MOUNT_THERMOMETER | QUALITROL 105 Remote Mount Thermometer | PF_TR_TEMP | MET_SENSOR_COUNT | Number of switches available |  | 3 | Up to 3 (2 adjustable and 1 fixed) | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/105_Remote_Mount_Thermometer_b568f343.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Number of switches available Up to 3 (2 adjustable and 1 fixed)
PROD_PDF_QUALITROL_105_REMOTE_MOUNT_THERMOMETER | QUALITROL 105 Remote Mount Thermometer | PF_TR_TEMP | MET_CONTACT_TYPE | Switch type |  |  | Snap action, SPST or SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/105_Remote_Mount_Thermometer_b568f343.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch type Snap action, SPST or SPDT
PROD_PDF_QUALITROL_105_REMOTE_MOUNT_THERMOMETER | QUALITROL 105 Remote Mount Thermometer | PF_TR_TEMP | MET_AMBIENT_TEMP | Std. operating temperatures | -34 | 60 | -30 to 140ºF (-34 to 60ºC) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/105_Remote_Mount_Thermometer_b568f343.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Std. operating temperatures -30 to 140ºF. (-34 to 60ºC)
PROD_PDF_QUALITROL_105_REMOTE_MOUNT_THERMOMETER | QUALITROL 105 Remote Mount Thermometer | PF_TR_TEMP | MET_ENCLOSURE_RATING | Case style |  |  | Vented case (standard) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/105_Remote_Mount_Thermometer_b568f343.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Case style Vented case (standard)
PROD_PDF_QUALITROL_120 | Qualitrol 120 | PF_TR_TEMP | MET_OIL_TEMPERATURE | Standard measurement ranges | 0 | 250 | 1-120, 0-160, 0-180, 20-180, 0-200, 0-220, 0-250 ºC | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/120_Bourdon_Tube_Thermometer_a5e8092f.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Standard measurement ranges 1-120, 0-160... 0-250 (ºC)
PROD_PDF_QUALITROL_120 | Qualitrol 120 | PF_TR_TEMP | MET_CONTACT_TYPE | Switch options |  |  | Snap-action, SPST or SPDT (UL recognized/CSA certified) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/120_Bourdon_Tube_Thermometer_a5e8092f.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Snap-action, SPST or SPDT (UL recognized/CSA certified)
PROD_PDF_QUALITROL_120 | Qualitrol 120 | PF_TR_TEMP | MET_CONTACT_TYPE | Number of switches |  | 4 | Up to four (4) | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/120_Bourdon_Tube_Thermometer_a5e8092f.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Number of switches Up to four (4)
PROD_PDF_QUALITROL_120 | Qualitrol 120 | PF_TR_TEMP | MET_ALARM_THRESHOLD | Switch differential | 5 | 10 | 5-10ºC standard | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/120_Bourdon_Tube_Thermometer_a5e8092f.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch differential 5-10ºC standard
PROD_PDF_QUALITROL_120 | Qualitrol 120 | PF_TR_TEMP | MET_AMBIENT_TEMP | Ambient operating temperature | -34 | 60 | -30 to 140°F (-34 to +60ºC) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/120_Bourdon_Tube_Thermometer_a5e8092f.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient operating temperature -30 to 140°F (-34 to +60ºC)
PROD_PDF_QUALITROL_120 | Qualitrol 120 | PF_TR_TEMP | MET_HUMIDITY | Relative humidity |  | 90 | 90% (non-condensing) | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/120_Bourdon_Tube_Thermometer_a5e8092f.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Relative humidity 90% (non-condensing)
PROD_PDF_QUALITROL_120 | Qualitrol 120 | PF_TR_TEMP | MET_VIBRATION | Vibration | 60 | 120 | 60 to 120 Hz @ 0.004" displacement | Hz |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/120_Bourdon_Tube_Thermometer_a5e8092f.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Vibration 60 to 120 Hz @ 0.004" displacement
PROD_PDF_QUALITROL_120 | Qualitrol 120 | PF_TR_TEMP | MET_ENCLOSURE_RATING | Housing material |  |  | Powder coated die-cast aluminum | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/120_Bourdon_Tube_Thermometer_a5e8092f.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Housing Powder coated die-cast aluminum
PROD_PDF_QUALITROL_130 | QUALITROL 130 | PF_TR_TEMP | MET_SENSOR_TYPE | RTD type |  |  | Pt100 (platinum 100 ohms) or Cu10 (copper 10 ohms) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/130_Thermal_Plate_0dbe066d.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: 1 or 2 (platinum [100 ohms] or copper [10 ohms])
PROD_PDF_QUALITROL_130 | QUALITROL 130 | PF_TR_TEMP | MET_SENSOR_COUNT | Number of RTDs | 1 | 2 | 1 or 2 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/130_Thermal_Plate_0dbe066d.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Number of RTDs 1 or 2
PROD_PDF_QUALITROL_130 | QUALITROL 130 | PF_TR_TEMP | MET_WINDING_TEMP | Winding temperature rise calibration range | 0 | 38 | 0 to 38ºC at 30ºC oil temperature | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/130_Thermal_Plate_0dbe066d.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Winding temperature rise adjustable from 0 to 38ºC
PROD_PDF_QUALITROL_130 | QUALITROL 130 | PF_TR_TEMP | MET_OIL_TEMPERATURE | Oil temperature range | -40 | 135 | -40 to 275ºF (-40 to +135ºC) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/130_Thermal_Plate_0dbe066d.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Oil temperature range -40 to 275ºF. (-40 to +135ºC)
PROD_PDF_QUALITROL_130 | QUALITROL 130 | PF_TR_TEMP | MET_AMBIENT_TEMP | Operating temperature | -40 | 70 | -40 to 158ºF (-40 to +70ºC) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/130_Thermal_Plate_0dbe066d.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Std. operating temperatures -40 to +70ºC
PROD_PDF_QUALITROL_130 | QUALITROL 130 | PF_TR_TEMP | MET_HUMIDITY | Ambient humidity | 0 | 95 | 0 - 95% non-condensing | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/130_Thermal_Plate_0dbe066d.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Ambient humidity 0 - 95% non-condensing
PROD_PDF_QUALITROL_130 | QUALITROL 130 | PF_TR_TEMP | MET_ENCLOSURE_RATING | Weatherproof rating |  |  | DIN 40050 IP54 compliant (NEMA 3R) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/130_Thermal_Plate_0dbe066d.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Weatherproof DIN 40050 IP54 compliant (NEMA 3R)
PROD_PDF_QUALITROL_130 | QUALITROL 130 | PF_TR_TEMP | MET_CURRENT_CHANNELS | CT current |  |  | 1 amp nominal (2 amps max overload) | A |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/130_Thermal_Plate_0dbe066d.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: CT current 1 amps nominal (2 amps MAXIMUM under overload)
PROD_PDF_QUALITROL_THERMAL_PLATE | QUALITROL Thermal Plate | PF_TR_TEMP | MET_SENSOR_COUNT | Number of wells | 1 | 3 | 1, 2 or 3 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/130_Thermal_Plate_0dbe066d.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Number of wells 1, 2 or 3
PROD_PDF_QUALITROL_THERMAL_PLATE | QUALITROL Thermal Plate | PF_TR_TEMP | MET_CURRENT_CHANNELS | CT current |  |  | 5 amps | A |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/130_Thermal_Plate_0dbe066d.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: CT current 5 amps
PROD_PDF_QUALITROL_THERMAL_PLATE | QUALITROL Thermal Plate | PF_TR_TEMP | MET_SENSOR_TYPE | Heating element material |  |  | Nickel alloy | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/130_Thermal_Plate_0dbe066d.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Heating element Nickel alloy
PROD_PDF_QUALITROL_141 | Qualitrol 141 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type |  |  | SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch type SPDT
PROD_PDF_QUALITROL_141 | Qualitrol 141 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Std. operating temperatures | -29 | 74 | -20 to +165°F (-29 to +74°C) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Std. operating temperatures -20 to +165°F
PROD_PDF_QUALITROL_141 | Qualitrol 141 | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Enclosure (141-005 only) |  |  | Optional, rated up to IP55 (NEMA 4) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Enclosure (141-005 only) Optional, rated up to IP55
PROD_PDF_QUALITROL_146 | Qualitrol 146 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type |  |  | SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch type SPDT
PROD_PDF_QUALITROL_146 | Qualitrol 146 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Std. operating temperatures | -29 | 74 | -20 to 165°F (-29 to 74°C) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Std. operating temperatures -20 to 165°F
PROD_PDF_QUALITROL_146 | Qualitrol 146 | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Enclosure |  |  | Optional, rated up to IP11 (NEMA 2) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Enclosure Optional, rated up to IP11 (NEMA 2)
PROD_PDF_QUALITROL_148 | Qualitrol 148 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type |  |  | SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Switch type SPDT
PROD_PDF_QUALITROL_148 | Qualitrol 148 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Std. operating temperatures | -40 | 82 | -40 to +180°F (-40 to +82°C) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Std. operating temperatures -40 to +180°F (-40 to +82°C)
PROD_PDF_QUALITROL_148 | Qualitrol 148 | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Enclosure |  |  | Standard IP11 (NEMA 2); IP55 (NEMA 4) optional | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Enclosure Standard, IP11 (NEMA 2); IP55 (NEMA 4) optional
PROD_PDF_QUALITROL_AKM_35600 | Qualitrol AKM 35600 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type |  |  | SPST or SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Switch type SPST or SPDT
PROD_PDF_QUALITROL_AKM_35600 | Qualitrol AKM 35600 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Std. operating temperatures | -40 | 80 | -40 to 176ºF (-40 to +80ºC) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Std. operating temperatures -40 to 176ºF (-40 to +80ºC)
PROD_PDF_QUALITROL_AKM_35600 | Qualitrol AKM 35600 | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Case |  |  | Weatherproof case IP55 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: comes standard with a weather proof case (IP55)
PROD_PDF_QUALITROL_47500 | Qualitrol 47500 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type |  |  | SPST or SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Switch type SPST or SPDT
PROD_PDF_QUALITROL_47500 | Qualitrol 47500 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Std. operating temperatures | -40 | 80 | -40 to 176ºF (-40 to +80ºC) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Std. operating temperatures -40 to 176ºF (-40 to +80ºC)
PROD_PDF_QUALITROL_150_151_DIRECT_MOUNT_THERMOMETERS | QUALITROL 150/151 Direct Mount Thermometers | PF_TR_TEMP | MET_AMBIENT_TEMP | Ambient operating temperatures | -40 | 60 | -40 to +60°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/150151_Indication_Only_Temperature_Indicator_99461e24.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient operating temperatures -40 to 140°F (-40 to +60°C)
PROD_PDF_QUALITROL_150_151_DIRECT_MOUNT_THERMOMETERS | QUALITROL 150/151 Direct Mount Thermometers | PF_TR_TEMP | MET_HUMIDITY | Ambient humidity |  | 90 | Up to 90% relative humidity | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/150151_Indication_Only_Temperature_Indicator_99461e24.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient humidity Up to 90% relative humidity
PROD_PDF_QUALITROL_150_151_DIRECT_MOUNT_THERMOMETERS | QUALITROL 150/151 Direct Mount Thermometers | PF_TR_TEMP | MET_ENCLOSURE_RATING | Case/Bezel materials |  |  | Stainless steel case and bezel | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/150151_Indication_Only_Temperature_Indicator_99461e24.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Case Stainless steel; Bezel Stainless steel
PROD_PDF_QUALITROL_165_167 | QUALITROL 165/167 | PF_TR_TEMP | MET_OIL_TEMPERATURE | Standard dial ranges | 0 | 250 | 0-120, 0-160, 0-180, 20-180, 0-200, 0-220, 0-250 ºC | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Standard dial ranges 0-120ºc ... 0-250ºC
PROD_PDF_QUALITROL_165_167 | QUALITROL 165/167 | PF_TR_TEMP | MET_ALARM_THRESHOLD | Accuracy |  |  | +/- 2% of dial range | % of dial range |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Accuracy +/- 2% of dial range
PROD_PDF_QUALITROL_165_167 | QUALITROL 165/167 | PF_TR_TEMP | MET_SENSOR_COUNT | Maximum number of switches |  | 3 | 3 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Maximum number of switches 3
PROD_PDF_QUALITROL_165_167 | QUALITROL 165/167 | PF_TR_TEMP | MET_CONTACT_TYPE | Switch type |  |  | SPST or SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch type SPST or SPDT
PROD_PDF_QUALITROL_165_167 | QUALITROL 165/167 | PF_TR_TEMP | MET_POWER_SUPPLY | Switch rating (AC) |  |  | 10A @ 125, 250 & 480 VAC | V AC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 10A @ 125, 250 & 480 VAC
PROD_PDF_QUALITROL_165_167 | QUALITROL 165/167 | PF_TR_TEMP | MET_POWER_SUPPLY | Switch rating (DC) |  |  | 1/2A @ 125 VDC; 1/4A @ 250 VDC; 1 1/2A @ 48 VDC | V DC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 1/2A @ 125 VDC - resistive
PROD_PDF_QUALITROL_165_167 | QUALITROL 165/167 | PF_TR_TEMP | MET_AMBIENT_TEMP | Std. operating temperatures | -34 | 60 | -30 to 140°F (-34 to 60°C) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Std. operating temperatures -30 to 140° F. (-34 to 60° C)
PROD_PDF_QUALITROL_165_167 | QUALITROL 165/167 | PF_TR_TEMP | MET_ENCLOSURE_RATING | Mounting |  |  | Side (center back thread) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting Side (center back thread)
PROD_PDF_QUALITROL_165_167 | QUALITROL 165/167 | PF_TR_TEMP | MET_PROTOCOL | Electrical connections |  |  | QUALITROL, military, ANSI, terminal block and flying leads | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Electrical connections QUALITROL, military, ANSI, terminal block
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_OIL_TEMPERATURE | Dial range | 0 | 150 | 0-150ºC | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dial range 0-150ºC
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_ALARM_THRESHOLD | Accuracy |  |  | +/- 2% of dial range | % of dial range |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Accuracy +/- 2% of dial range
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_SENSOR_COUNT | Maximum number of switches |  | 2 | 2 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Maximum number of switches 2
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_CONTACT_TYPE | Switch type |  |  | SPST or SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch type SPST or SPDT
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_POWER_SUPPLY | Switch rating (AC) |  |  | 5A @ 250 VAC | V AC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 5A @ 250 VAC
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_POWER_SUPPLY | Switch rating (DC) |  |  | 0.3A @ 110 VDC - inductive | V DC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (DC) 0.3A @ 110 VDC - inductive
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_AMBIENT_TEMP | Std. operating temperatures | -40 | 70 | -40 to 158ºF (-40 to 70ºC) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Std. operating temperatures -40 to 158ºF (-40 to 70ºC)
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_PROTOCOL | Electrical connections |  |  | Terminal block | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Electrical connections Terminal block
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_ENCLOSURE_RATING | Mounting |  |  | Side (center back thread) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting Side (center back thread)
PROD_PDF_QUALITROL_201_SERIES | Qualitrol 201 Series | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Standard operating temperature | -29 | 105 | -20 to 220ºF (-29 to 105ºC) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/201_Pressure_Relief_Valves_d1b1429e.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Standard operating temperature -20 to 220ºF (-29 to 105ºC)
PROD_PDF_QUALITROL_202_SERIES | Qualitrol 202 Series | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Standard operating temperature | -29 | 105 | -20 to 220ºF (-29 to 105ºC) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/201_Pressure_Relief_Valves_d1b1429e.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Standard operating temperature -20 to 220ºF (-29 to 105ºC)
PROD_PDF_QUALITROL_205_SERIES | Qualitrol 205 Series | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Standard operating temperature | -29 | 105 | -20 to 220ºF (-29 to 105ºC) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/201_Pressure_Relief_Valves_d1b1429e.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Standard operating temperature -20 to 220ºF (-29 to 105ºC)
PROD_PDF_QUALITROL_206 | Qualitrol 206 | PF_AUX_SENSOR | MET_ALARM_THRESHOLD | Operating pressure range 1 | 2.9 | 5.7 | 2.9 to 5.7 PSI | PSI |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/206_Medium_Pressure_Relief_Device_(MPRD)_8039338a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: adjustable in three ranges (2.9 to 5.7 PSI
PROD_PDF_QUALITROL_206 | Qualitrol 206 | PF_AUX_SENSOR | MET_ALARM_THRESHOLD | Operating pressure range 2 | 5.8 | 8.6 | 5.8 to 8.6 PSI | PSI |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/206_Medium_Pressure_Relief_Device_(MPRD)_8039338a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 5.8 to 8.6 PSI and 8.7 to 11.6 PSI
PROD_PDF_QUALITROL_206 | Qualitrol 206 | PF_AUX_SENSOR | MET_ALARM_THRESHOLD | Operating pressure range 3 | 8.7 | 11.6 | 8.7 to 11.6 PSI | PSI |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/206_Medium_Pressure_Relief_Device_(MPRD)_8039338a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 8.7 to 11.6 PSI
PROD_PDF_QUALITROL_206 | Qualitrol 206 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Alarm switches |  |  | Up to two switches for alarm and control functions | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/206_Medium_Pressure_Relief_Device_(MPRD)_8039338a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Available with up to two switches for alarm and control functions
PROD_PDF_QUALITROL_206 | Qualitrol 206 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch ratings |  |  | 6 A @ 120 VAC, 3 A @ 240 VAC, 0.55 A @ 125 VDC, 0.27 A @ 250 VDC resistive | A/V |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/206_Medium_Pressure_Relief_Device_(MPRD)_8039338a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 6 A @ 120 VAC, 3 A @ 240 VAC, 0.55 A @ 125 VDC
PROD_PDF_QUALITROL_206 | Qualitrol 206 | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Switch enclosure rating |  |  | IP67 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/206_Medium_Pressure_Relief_Device_(MPRD)_8039338a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch enclosure Meets IP67 requirements
PROD_PDF_QUALITROL_206 | Qualitrol 206 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Ambient operating temperature | -40 | 80 | -40°C to +80°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/206_Medium_Pressure_Relief_Device_(MPRD)_8039338a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient operating temperature -40°C to +80°C
PROD_PDF_QUALITROL_206 | Qualitrol 206 | PF_AUX_SENSOR | MET_OIL_TEMPERATURE | Oil operating temperature | -20 | 100 | -20°C to +100°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/206_Medium_Pressure_Relief_Device_(MPRD)_8039338a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Oil operating temperature -20°C to +100°C
PROD_PDF_QUALITROL_206 | Qualitrol 206 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Switch operating temperature | -25 | 85 | -25°C to +85°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/206_Medium_Pressure_Relief_Device_(MPRD)_8039338a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch operating temperature -25°C to +85°C
PROD_PDF_QUALITROL_070_351_PRESSURE_VACUUM_BLEEDERS | QUALITROL 070/351 Pressure-Vacuum Bleeders | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Ambient operating temperatures | -40 | 70 | -40°F to 158°F (-40ºC to 70ºC) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/351_PressureVacuum_Gauge_and_Bleeders_724e62e8.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient operating temperatures -40°F to 158°F
PROD_PDF_QUALITROL_T_GUARD_408 | Qualitrol T/Guard 408 | PF_TR_TEMP | MET_SENSOR_COUNT | Number of optical channels | 4 | 16 | 4, 6, 8, 10, 12, 14 or 16 optical channels | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 4, 6, 8, 10, 12, 14 or 16 optical channels
PROD_PDF_QUALITROL_T_GUARD_408 | Qualitrol T/Guard 408 | PF_TR_TEMP | MET_WINDING_TEMP | Temperature measurement range | -50 | 200 | -50°C to 200°C (-58°F to 392°F) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: -50°C to 200°C (-58°F to 392°F)
PROD_PDF_QUALITROL_T_GUARD_408 | Qualitrol T/Guard 408 | PF_TR_TEMP | MET_SAMPLING_RATE | System sampling rate |  |  | 250 ms switching rate between each channel | ms |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 250 ms switching rate between each channel
PROD_PDF_QUALITROL_T_GUARD_408 | Qualitrol T/Guard 408 | PF_TR_TEMP | MET_PROTOCOL | Serial communication protocols |  |  | ASCII, Modbus RTU, DNP 3.0 (optional) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: ASCII; Modbus RTU (2 or 4-wire config); DNP 3.0 (optional)
PROD_PDF_QUALITROL_T_GUARD_408 | Qualitrol T/Guard 408 | PF_TR_TEMP | MET_NETWORK | Communication hardware |  |  | Isolated RS-485 serial port | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Isolated RS-485 serial port on screw terminal
PROD_PDF_QUALITROL_T_GUARD_408 | Qualitrol T/Guard 408 | PF_TR_TEMP | MET_CONTACT_TYPE | Relays |  |  | 8 Form-C (SPDT) relays plus 9th system fault relay | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 8 built-in relay drivers; Form-C (SPDT) relays
PROD_PDF_QUALITROL_T_GUARD_408 | Qualitrol T/Guard 408 | PF_TR_TEMP | MET_POWER_SUPPLY | Power requirements |  |  | 95-240 Vac 50/60Hz or 135-240 Vdc, ±10% | V AC/DC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 95 - 240 Vac, 50/60 Hz or 135 - 240 Vdc
PROD_PDF_QUALITROL_T_GUARD_408 | Qualitrol T/Guard 408 | PF_TR_TEMP | MET_AMBIENT_TEMP | Operating temperature | -40 | 72 | -40 to +72°C, 5-90% humidity, non-condensing | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: -40 to +72°C, 5-90% humidity, non-condensing
PROD_PDF_QUALITROL_T_GUARD_408 | Qualitrol T/Guard 408 | PF_TR_TEMP | MET_ENCLOSURE_RATING | Enclosure rating |  |  | NEMA-4 enclosure (NEMA/EEMAC Type 4 and 12) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: mounted in a NEMA-4 enclosure ... compliant with NEMA/EEMAC Type 4 and 12
PROD_PDF_QUALITROL_T_GUARD_408 | Qualitrol T/Guard 408 | PF_TR_TEMP | MET_SENSOR_TYPE | Probe compatibility |  |  | Qualitrol/Neoptix GaAs fiber optic temperature probes | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Compatible with all Qualitrol / Neoptix GaAs fiber optic temperature probes
PROD_PDF_QUALITROL_T_GUARD_408XT | Qualitrol T/Guard 408XT | PF_TR_TEMP | MET_SENSOR_COUNT | Number of optical channels | 4 | 16 | 4, 6, 8, 10, 12, 14 or 16 optical channels | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 4, 6, 8, 10, 12, 14 or 16 optical channels
PROD_PDF_QUALITROL_T_GUARD_408XT | Qualitrol T/Guard 408XT | PF_TR_TEMP | MET_WINDING_TEMP | Temperature measurement range | -50 | 200 | -50°C to 200°C (-58°F to 392°F) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: -50°C to 200°C (-58°F to 392°F)
PROD_PDF_QUALITROL_T_GUARD_408XT | Qualitrol T/Guard 408XT | PF_TR_TEMP | MET_PROTOCOL | Ethernet communication protocols |  |  | HTTP, Modbus over Ethernet, DNP 3.0, IEC 60870-5-104, IEC 61850 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: HTTP; Modbus over Ethernet; DNP 3.0; IEC 60870-5-104; IEC 61850
PROD_PDF_QUALITROL_T_GUARD_408XT | Qualitrol T/Guard 408XT | PF_TR_TEMP | MET_NETWORK | Communication hardware |  |  | RS-485; Ethernet 10/100BASE-T; option 100BASE-FX | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Ethernet 10/100BASE-T; Option: Ethernet 100BASE-FX
PROD_PDF_QUALITROL_T_GUARD_408XT | Qualitrol T/Guard 408XT | PF_TR_TEMP | MET_SAMPLING_RATE | System sampling rate |  |  | 250 ms switching rate between each channel | ms |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 250 ms switching rate between each channel
PROD_PDF_QUALITROL_T_GUARD_408XT | Qualitrol T/Guard 408XT | PF_TR_TEMP | MET_CONTACT_TYPE | Relays |  |  | 8 Form-C (SPDT) relays plus 9th system fault relay | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 8 built-in relay drivers ... 9th built-in relay for dedicated system fault
PROD_PDF_QUALITROL_T_GUARD_408XT | Qualitrol T/Guard 408XT | PF_TR_TEMP | MET_POWER_SUPPLY | Power requirements |  |  | 95-240 Vac 50/60Hz or 135-240 Vdc, ±10% | V AC/DC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 95 - 240 Vac, 50/60 Hz or 135 - 240 Vdc
PROD_PDF_QUALITROL_T_GUARD_408XT | Qualitrol T/Guard 408XT | PF_TR_TEMP | MET_AMBIENT_TEMP | Operating temperature | -40 | 72 | -40 to +72°C, 5-90% humidity, non-condensing | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: -40 to +72°C, 5-90% humidity, non-condensing
PROD_PDF_QUALITROL_T_GUARD_408XT | Qualitrol T/Guard 408XT | PF_TR_TEMP | MET_ENCLOSURE_RATING | Enclosure rating |  |  | NEMA-4 enclosure (NEMA/EEMAC Type 4 and 12) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: NEMA-4 enclosure ... compliant with NEMA/EEMAC Type 4 and 12
PROD_PDF_QUALITROL_900_RPRR | QUALITROL 900 RPRR | PF_AUX_SENSOR | MET_ASSET_TYPE | Application space |  |  | Oil space | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 900 = Oil
PROD_PDF_QUALITROL_900_RPRR | QUALITROL 900 RPRR | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Ingress protection |  |  | IP65 (standard) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Ingress Protection IP65 (standard)
PROD_PDF_QUALITROL_900_RPRR | QUALITROL 900 RPRR | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Ambient operating temperature | -40 | 82 | -40°C to 82°C standard, -55°C option | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Ambient operating temperatures -40°F to 180°F (-40°C to 82ºC) standard
PROD_PDF_QUALITROL_900_RPRR | QUALITROL 900 RPRR | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type |  |  | Snap action, SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Switch type Snap action, SPDT
PROD_PDF_QUALITROL_900_RPRR | QUALITROL 900 RPRR | PF_AUX_SENSOR | MET_POWER_SUPPLY | Switch rating AC |  |  | 10 A @ 120, 240 & 480 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 10 A @ 120, 240 & 480 VAC
PROD_PDF_QUALITROL_900_RPRR | QUALITROL 900 RPRR | PF_AUX_SENSOR | MET_POWER_SUPPLY | Switch rating DC |  |  | ½ A @ 125 VDC, ¼ A @ 250 VDC resistive | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Switch rating (DC) ½ A @ 125 VDC - resistive
PROD_PDF_QUALITROL_910_RPRR | QUALITROL 910 RPRR | PF_AUX_SENSOR | MET_ASSET_TYPE | Application space |  |  | Gas space | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 910 = Gas
PROD_PDF_QUALITROL_910_RPRR | QUALITROL 910 RPRR | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Ingress protection |  |  | IP65 (standard) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Ingress Protection IP65 (standard)
PROD_PDF_QUALITROL_910_RPRR | QUALITROL 910 RPRR | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Ambient operating temperature | -40 | 82 | -40°C to 82°C standard, -55°C option | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Ambient operating temperatures -40°F to 180°F (-40°C to 82ºC) standard
PROD_PDF_QUALITROL_910_RPRR | QUALITROL 910 RPRR | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type |  |  | Snap action, SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Switch type Snap action, SPDT
PROD_PDF_QUALITROL_910_RPRR | QUALITROL 910 RPRR | PF_AUX_SENSOR | MET_POWER_SUPPLY | Switch rating AC |  |  | 10 A @ 120, 240 & 480 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 10 A @ 120, 240 & 480 VAC
PROD_PDF_QUALITROL_910_RPRR | QUALITROL 910 RPRR | PF_AUX_SENSOR | MET_POWER_SUPPLY | Switch rating DC |  |  | ½ A @ 125 VDC, ¼ A @ 250 VDC resistive | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Switch rating (DC) ½ A @ 125 VDC - resistive
PROD_PDF_QUALITROL_909_300_01 | Qualitrol 909-300-01 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Relay Types |  |  | (1) Form A and (1) Form C | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/909_Seal-In_Relay_a0e59e43.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Relay Types (1) Form A and (1) Form C
PROD_PDF_QUALITROL_909_300_01 | Qualitrol 909-300-01 | PF_AUX_SENSOR | MET_POWER_SUPPLY | Input Voltages |  |  | 24, 48, 125 VDC, 120 VAC | V AC/DC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/909_Seal-In_Relay_a0e59e43.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 909-300-01 -- 24, 48, 125 VDC, 120 VAC
PROD_PDF_QUALITROL_909_300_01 | Qualitrol 909-300-01 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Trip Contact Rating |  |  | 1/4 HP @ 125/250 VAC; 8A @ 250 VAC; 8A @ 30 VDC resistive | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/909_Seal-In_Relay_a0e59e43.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Trip Contact Rating 1/4 HP @ 125/250 VAC 8A @ 250 VAC
PROD_PDF_QUALITROL_909_300_01 | Qualitrol 909-300-01 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Alarm Contact Rating |  |  | 1/4 HP @ 125/250 VAC; 8A @ 250 VAC; 8A @ 30 VDC resistive | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/909_Seal-In_Relay_a0e59e43.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Alarm Contact Rating 1/4 HP @ 125/250 VAC
PROD_PDF_QUALITROL_909_300_01 | Qualitrol 909-300-01 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Ambient Operating Temperature | -45 | 40 | -49 to 104°F (-45 to 40°C) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/909_Seal-In_Relay_a0e59e43.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient Operating Temperatures -49 to 104°F (-45 to 40°C)
PROD_PDF_QUALITROL_909_300_01 | Qualitrol 909-300-01 | PF_AUX_SENSOR | MET_HUMIDITY | Ambient Humidity |  | 95 | 95% non-condensing | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/909_Seal-In_Relay_a0e59e43.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient Humidity 95% non-condensing
PROD_PDF_QUALITROL_909_300_01 | Qualitrol 909-300-01 | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Mounting |  |  | Surface mounted inside an IP rated enclosure | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/909_Seal-In_Relay_a0e59e43.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Designed to be surface mounted inside an IP rated enclosure
PROD_PDF_QUALITROL_909_300_02 | Qualitrol 909-300-02 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Relay Types |  |  | (1) Form A and (1) Form C | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/909_Seal-In_Relay_a0e59e43.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Relay Types (1) Form A and (1) Form C
PROD_PDF_QUALITROL_909_300_02 | Qualitrol 909-300-02 | PF_AUX_SENSOR | MET_POWER_SUPPLY | Input Voltages |  |  | 48, 125, 250 VDC, 120, 240 VAC | V AC/DC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/909_Seal-In_Relay_a0e59e43.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 909-300-02 -- 48, 125, 250 VDC, 120, 240 VAC
PROD_PDF_QUALITROL_909_300_02 | Qualitrol 909-300-02 | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Hazardous Location Rating |  |  | UL1604 class I, division II hazardous locations | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/909_Seal-In_Relay_a0e59e43.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 909-300-02 is additionally listed for UL1604 class I, division II
PROD_PDF_QUALITROL_909_300_02 | Qualitrol 909-300-02 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Ambient Operating Temperature | -45 | 40 | -49 to 104°F (-45 to 40°C) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/909_Seal-In_Relay_a0e59e43.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient Operating Temperatures -49 to 104°F (-45 to 40°C)
PROD_PDF_QUALITROL_909_300_02 | Qualitrol 909-300-02 | PF_AUX_SENSOR | MET_HUMIDITY | Ambient Humidity |  | 95 | 95% non-condensing | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/909_Seal-In_Relay_a0e59e43.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient Humidity 95% non-condensing
PROD_PDF_QUALITROL_930 | Qualitrol 930 | PF_AUX_SENSOR | MET_SENSOR_TYPE | Pressure sensors |  |  | Electronic pressure sensors continuously output current pressure level | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/930_Electronic_Pressure_Monitor_f58007ab.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Electronic pressure sensors continuously output current pressure level
PROD_PDF_QUALITROL_930 | Qualitrol 930 | PF_AUX_SENSOR | MET_SENSOR_COUNT | Multi-sensor logic |  |  | 2 of 3 logic; 3 pressure sensors | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/930_Electronic_Pressure_Monitor_f58007ab.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 2 of 3 logic to trigger a trip signal only if 2 of the 3 pressure sensors
PROD_PDF_QUALITROL_930 | Qualitrol 930 | PF_AUX_SENSOR | MET_ALARM_THRESHOLD | Slow pressure actuation range | 1 | 15 | Adjustable from 1-15 PSIG (0-1 bar) | PSIG |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/930_Electronic_Pressure_Monitor_f58007ab.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Slow pressure: Adjustable from 1-15 PSIG (0-1 bar) for actuation
PROD_PDF_QUALITROL_930 | Qualitrol 930 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Relay outputs |  |  | Up to 9 SPDT relays (6 fast, 2 slow, 1 power status) | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/930_Electronic_Pressure_Monitor_f58007ab.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Up to 9 SPDT relays (6 for fast pressure rise, 2 for slow pressure rise, 1 for power status)
PROD_PDF_QUALITROL_930 | Qualitrol 930 | PF_AUX_SENSOR | MET_PROTOCOL | Remote output signal |  |  | 0-1 mA (12,000Ω max) or 4-20 mA (600Ω max) | mA |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/930_Electronic_Pressure_Monitor_f58007ab.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 0 to 1 mA (12,000Ω max load) 4 to 20 mA (600 Ω max. load)
PROD_PDF_QUALITROL_930 | Qualitrol 930 | PF_AUX_SENSOR | MET_POWER_SUPPLY | Universal input power |  |  | 85-265 VAC 50/60 Hz or 110-370 VDC | V AC/DC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/930_Electronic_Pressure_Monitor_f58007ab.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Universal: 85-265 VAC 50-60 Hz, or 110-370 VDC
PROD_PDF_QUALITROL_930 | Qualitrol 930 | PF_AUX_SENSOR | MET_POWER_SUPPLY | Pre-configured input power |  |  | 120/240 VAC 50-60 Hz, 125/250 VDC, or 36-72 VDC | V AC/DC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/930_Electronic_Pressure_Monitor_f58007ab.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Pre-configured: 120/240 VAC 50-60 Hz, 125/250 VDC, or 36-72 VDC
PROD_PDF_QUALITROL_930 | Qualitrol 930 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Sensor operating temperature | -40 | 85 | -40°C to 85°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/930_Electronic_Pressure_Monitor_f58007ab.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Sensor and cable: -40°F to 185°F (-40°C to to 85°C)
PROD_PDF_QUALITROL_930 | Qualitrol 930 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Control board operating temperature | -30 | 72 | -30°C to 72°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/930_Electronic_Pressure_Monitor_f58007ab.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Control board: -22°F to 162°F (-30°C to 72°C)
PROD_PDF_QUALITROL_930 | Qualitrol 930 | PF_AUX_SENSOR | MET_HUMIDITY | Relative humidity | 10 | 90 | 10% to 90% non-condensing | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/930_Electronic_Pressure_Monitor_f58007ab.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Relative humidity 10% to 90% non-condensing
PROD_PDF_QUALITROL_AKM345_GEN3_OTIWTI | Qualitrol AKM345 Gen3 OTIWTI | PF_TR_TEMP | MET_OIL_TEMPERATURE | Standard Measurement Range | 0 | 150 | 0°C to 150°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM345_Gen3_Oil_and_Winding_Temperature_Indicator_09e05650.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Standard Measurement Range 0°C to 150°C
PROD_PDF_QUALITROL_AKM345_GEN3_OTIWTI | Qualitrol AKM345 Gen3 OTIWTI | PF_TR_TEMP | MET_WINDING_TEMP | Winding Temperature Simulation |  |  | Internal option: CT ≤ 2.2A, CT ≤ 2.65A, or CT ≤ 5A | A |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM345_Gen3_Oil_and_Winding_Temperature_Indicator_09e05650.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Internal option for: CT ≤ 2.2A, CT ≤ 2.65A, or CT ≤ 5A
PROD_PDF_QUALITROL_AKM345_GEN3_OTIWTI | Qualitrol AKM345 Gen3 OTIWTI | PF_TR_TEMP | MET_CONTACT_TYPE | Switch Types |  |  | Standard, High-DC, and Gold options | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM345_Gen3_Oil_and_Winding_Temperature_Indicator_09e05650.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Switch Types Standard, High-DC, and Gold options
PROD_PDF_QUALITROL_AKM345_GEN3_OTIWTI | Qualitrol AKM345 Gen3 OTIWTI | PF_TR_TEMP | MET_PROTOCOL | Communications |  |  | RS-485 MODBUS | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM345_Gen3_Oil_and_Winding_Temperature_Indicator_09e05650.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Communications RS-485 MODBUS
PROD_PDF_QUALITROL_AKM345_GEN3_OTIWTI | Qualitrol AKM345 Gen3 OTIWTI | PF_TR_TEMP | MET_ENCLOSURE_RATING | Ingress Protection |  |  | IP66 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM345_Gen3_Oil_and_Winding_Temperature_Indicator_09e05650.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Ingress Protection IP66
PROD_PDF_QUALITROL_AKM345_GEN3_OTIWTI | Qualitrol AKM345 Gen3 OTIWTI | PF_TR_TEMP | MET_AMBIENT_TEMP | Ambient Operating Temperature | -40 | 70 | -40°C to 70°C standard; -60°C to 70°C Polar | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM345_Gen3_Oil_and_Winding_Temperature_Indicator_09e05650.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: -40°C to 70°C - Standard -60°C to 70°C - Polar
PROD_PDF_QUALITROL_AKM345_GEN3_OTIWTI | Qualitrol AKM345 Gen3 OTIWTI | PF_TR_TEMP | MET_HUMIDITY | Humidity |  | 95 | 95% non-condensing relative humidity @ 95°C | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM345_Gen3_Oil_and_Winding_Temperature_Indicator_09e05650.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 95% non-condensing relative humidity @ 95°C
PROD_PDF_QUALITROL_AKM_35600 | QUALITROL AKM 35600 | PF_AUX_SENSOR | MET_SENSOR_COUNT | Number of switches available | 2 | 3 | 2 or 3 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_35600_Pressure_Control_Switches_86b46020.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Number of switches available 2 or 3
PROD_PDF_QUALITROL_AKM_35600 | QUALITROL AKM 35600 | PF_AUX_SENSOR | MET_ALARM_THRESHOLD | Repeatability of switch set points |  |  | +/-5% or +/- 0.4 PSI (3 kPa) | %/PSI |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_35600_Pressure_Control_Switches_86b46020.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Repeatability of +/-5% or +/- 0.4 PSI (3 kPa)
PROD_PDF_QUALITROL_AKM_35600 | QUALITROL AKM 35600 | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Enclosure rating |  |  | IP55 weather proof case standard | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_35600_Pressure_Control_Switches_86b46020.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: comes standard with a weather proof case (IP55)
PROD_PDF_QUALITROL_AKM_35600 | QUALITROL AKM 35600 | PF_AUX_SENSOR | MET_POWER_SUPPLY | Switch rating (AC) |  |  | 5 A @ 125 VAC resistive; 3 A @ 250 VAC resistive | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_35600_Pressure_Control_Switches_86b46020.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 5 A @ 125 VAC resistive 3 A @ 250 VAC resistive
PROD_PDF_QUALITROL_141 | QUALITROL 141 | PF_AUX_SENSOR | MET_SENSOR_COUNT | Number of switches available |  |  | 2 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_35600_Pressure_Control_Switches_86b46020.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Number of switches available 2
PROD_PDF_QUALITROL_141 | QUALITROL 141 | PF_AUX_SENSOR | MET_POWER_SUPPLY | Switch rating (AC) |  |  | 15 A @ 125, 250, 480 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_35600_Pressure_Control_Switches_86b46020.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 15 A @ 125, 250, 480 VAC
PROD_PDF_QUALITROL_141 | QUALITROL 141 | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Enclosure |  |  | Optional, rated up to IP55 (NEMA 4) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_35600_Pressure_Control_Switches_86b46020.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Enclosure (141-005 only) Optional, rated up to IP55 (NEMA 4)
PROD_PDF_QUALITROL_146 | QUALITROL 146 | PF_AUX_SENSOR | MET_SENSOR_COUNT | Number of switches available |  |  | 1 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_35600_Pressure_Control_Switches_86b46020.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Number of switches available 1
PROD_PDF_QUALITROL_146 | QUALITROL 146 | PF_AUX_SENSOR | MET_POWER_SUPPLY | Switch rating (AC) |  |  | 15 A @ 115, 250 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_35600_Pressure_Control_Switches_86b46020.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 15 A @ 115, 250 VAC
PROD_PDF_QUALITROL_148 | QUALITROL 148 | PF_AUX_SENSOR | MET_SENSOR_COUNT | Number of switches available | 1 | 2 | 1 or 2 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_35600_Pressure_Control_Switches_86b46020.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Number of switches available 1 or 2
PROD_PDF_QUALITROL_148 | QUALITROL 148 | PF_AUX_SENSOR | MET_POWER_SUPPLY | Switch rating (AC) |  |  | 15 A @ 125, 250, 480 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_35600_Pressure_Control_Switches_86b46020.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 15 A @ 125, 250, 480 VAC
PROD_PDF_AKM_44611_48471 | AKM 44611/48471 | PF_TR_TEMP | MET_OIL_TEMPERATURE | Standard dial range | 10 | 120 | 10-120ºC | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_4461148471_Bi-Metal_Thermometer_71abb218.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Standard dial ranges 10-120ºC
PROD_PDF_AKM_44611_48471 | AKM 44611/48471 | PF_TR_TEMP | MET_ENCLOSURE_RATING | Enclosure rating |  |  | IP54 according to IEC 529 (equivalent NEMA 3S) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_4461148471_Bi-Metal_Thermometer_71abb218.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: IP54 according to IEC 529 (equivalent NEMA 3S rating)
PROD_PDF_AKM_44611_48471 | AKM 44611/48471 | PF_TR_TEMP | MET_AMBIENT_TEMP | Ambient operating temperature | -40 | 70 | -40 to +70 ºC | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_4461148471_Bi-Metal_Thermometer_71abb218.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient operating temperature -40 to +70 ºC
PROD_PDF_AKM_44612_44622_44617_44618_44650 | AKM 44612/44622/44617/44618/44650 | PF_TR_TEMP | MET_OIL_TEMPERATURE | Standard dial ranges | 10 | 120 | 10-120ºC, 0-130ºC, -20-120ºC, 60-150ºC | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_44612446224461744618_Thermometer_188b5fee.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Standard dial ranges 10-120ºC, 0-130ºC, -20-120ºC, 60-150ºC
PROD_PDF_AKM_44612_44622_44617_44618_44650 | AKM 44612/44622/44617/44618/44650 | PF_TR_TEMP | MET_WINDING_TEMP | Winding temperature simulation |  |  | Can be used to simulate winding temperature | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_44612446224461744618_Thermometer_188b5fee.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Heating element is built into the thermometer probe
PROD_PDF_AKM_44612_44622_44617_44618_44650 | AKM 44612/44622/44617/44618/44650 | PF_TR_TEMP | MET_CONTACT_TYPE | Number of switches |  | 2 | up to 2 (standard) | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_44612446224461744618_Thermometer_188b5fee.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Number of switches up to 2 (standard)
PROD_PDF_AKM_44612_44622_44617_44618_44650 | AKM 44612/44622/44617/44618/44650 | PF_TR_TEMP | MET_ALARM_THRESHOLD | Contact trigger range | 10 | 120 | anywhere within 10-120ºC | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_44612446224461744618_Thermometer_188b5fee.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Contacts can be set to trigger anywhere within the range of 10-120ºC
PROD_PDF_AKM_44612_44622_44617_44618_44650 | AKM 44612/44622/44617/44618/44650 | PF_TR_TEMP | MET_POWER_SUPPLY | Switch rating AC |  |  | 5A @ 250 VAC | V AC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_44612446224461744618_Thermometer_188b5fee.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 5A @ 250 VAC
PROD_PDF_AKM_44612_44622_44617_44618_44650 | AKM 44612/44622/44617/44618/44650 | PF_TR_TEMP | MET_POWER_SUPPLY | Switch rating DC |  |  | 0.3 A @ 110 VDC (L/R ≤ 10 ms) | V DC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_44612446224461744618_Thermometer_188b5fee.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (DC) 0.3 A @ 110 VDC
PROD_PDF_AKM_44612_44622_44617_44618_44650 | AKM 44612/44622/44617/44618/44650 | PF_TR_TEMP | MET_ENCLOSURE_RATING | Weather-proof rating |  |  | IEC 529 protective class IP55 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_44612446224461744618_Thermometer_188b5fee.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Weather-proof rating IEC 529 protective class IP55
PROD_PDF_AKM_44612_44622_44617_44618_44650 | AKM 44612/44622/44617/44618/44650 | PF_TR_TEMP | MET_AMBIENT_TEMP | Ambient operating temperature | -40 | 70 | -40 to 70°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_44612446224461744618_Thermometer_188b5fee.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient operating temperature -40 to +158 °F (-40 to 70°C.)
PROD_PDF_AKM_44612_44622_44617_44618_44650 | AKM 44612/44622/44617/44618/44650 | PF_TR_TEMP | MET_SENSOR_TYPE | SCADA output sensor |  |  | Pt100 electronic output | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_44612446224461744618_Thermometer_188b5fee.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: Available with a Pt100 electronic output for SCADA system integration
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_NETWORK | Electrical connections |  |  | Terminal block | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_47080_Direct_Mount_Bimetal_Thermometer_1a28ed38.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Electrical connections Terminal block
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_SENSOR_TYPE | Probe material |  |  | Stainless steel (standard) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_47080_Direct_Mount_Bimetal_Thermometer_1a28ed38.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Probe Stainless steel (standard)
PROD_PDF_QUALITROL_032_042_045_LARGE_OIL_LEVEL_INDICATOR | QUALITROL 032/042/045 Large Oil Level Indicator | PF_AUX_SENSOR | MET_SENSOR_TYPE | Float mechanism |  |  | Gear (042/045) or lever (032) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Float mechanism Gear (042 and 045 series) or lever (032 series)
PROD_PDF_QUALITROL_032_042_045_LARGE_OIL_LEVEL_INDICATOR | QUALITROL 032/042/045 Large Oil Level Indicator | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type |  |  | SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Switch type SPDT
PROD_PDF_QUALITROL_032_042_045_LARGE_OIL_LEVEL_INDICATOR | QUALITROL 032/042/045 Large Oil Level Indicator | PF_AUX_SENSOR | MET_PROTOCOL | SCADA output signal |  |  | 4-20mA or 0-1mA (with 039 Remote Enclosure) | mA |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Output signal 4 - 20mA or 0 - 1mA (Only with 039 Remote Enclosure)
PROD_PDF_QUALITROL_032_042_045_LARGE_OIL_LEVEL_INDICATOR | QUALITROL 032/042/045 Large Oil Level Indicator | PF_AUX_SENSOR | MET_POWER_SUPPLY | Supply voltage |  |  | 24 VDC nominal (120 or 240 VAC on 039 series) | V |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Supply voltage 24 VDC nominal (120 or 240 VAC on 039 series)
PROD_PDF_QUALITROL_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATOR | QUALITROL AKM 44712 / 34725 Large Oil Level Indicator | PF_AUX_SENSOR | MET_SENSOR_TYPE | Float mechanism |  |  | Gear (34725) or lever (44712) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Float mechanism Gear (34725) or lever (44712)
PROD_PDF_QUALITROL_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATOR | QUALITROL AKM 44712 / 34725 Large Oil Level Indicator | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type |  |  | SPST or SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch type SPST or SPDT
PROD_PDF_QUALITROL_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATOR | QUALITROL AKM 44712 / 34725 Large Oil Level Indicator | PF_AUX_SENSOR | MET_PROTOCOL | SCADA output signal |  |  | 4-20 mA | mA |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Output signal 4 - 20 mA
PROD_PDF_QUALITROL_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATOR | QUALITROL AKM 44712 / 34725 Large Oil Level Indicator | PF_AUX_SENSOR | MET_POWER_SUPPLY | Supply voltage |  |  | 24 VDC nominal | V |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Supply voltage 24 VDC nominal
PROD_PDF_AKM_OLR | AKM OLR | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Enclosure protection class |  |  | IP54, weather-proof per DIN 40050 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_OLR_Remote_Mechanical_Oil_Level_Indicator_ad31eee0.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: weather-proof according to DIN 40050 protection class IP 54
PROD_PDF_AKM_OLR | AKM OLR | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Ambient operating temperature | -50 | 70 | -58 to +158°F (-50 to +70°C) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_OLR_Remote_Mechanical_Oil_Level_Indicator_ad31eee0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient operating temperature -58 to +158°F (-50 to +70°C)
PROD_PDF_AKM_OLR | AKM OLR | PF_AUX_SENSOR | MET_HUMIDITY | Ambient humidity | 35 | 100 | 35% to 100% | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_OLR_Remote_Mechanical_Oil_Level_Indicator_ad31eee0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient humidity 35% to 100%
PROD_PDF_AKM_OLR | AKM OLR | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type |  |  | Magnetic blow-out | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_OLR_Remote_Mechanical_Oil_Level_Indicator_ad31eee0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch type Magnetic blow-out
PROD_PDF_AKM_OLR | AKM OLR | PF_AUX_SENSOR | MET_SENSOR_COUNT | Number of switches | 2 | 4 | 2 or 4 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_OLR_Remote_Mechanical_Oil_Level_Indicator_ad31eee0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Number of switches 2 or 4
PROD_PDF_AKM_OLR | AKM OLR | PF_AUX_SENSOR | MET_POWER_SUPPLY | Switch rating (AC) |  |  | 3A @ 220 VAC/VDC | V AC/DC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_OLR_Remote_Mechanical_Oil_Level_Indicator_ad31eee0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 3A @ 220 VAC/VDC
PROD_PDF_AKM_OLR | AKM OLR | PF_AUX_SENSOR | MET_PROTOCOL | Electronic output |  |  | 4-20mA output for remote indication and SCADA integration | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_OLR_Remote_Mechanical_Oil_Level_Indicator_ad31eee0.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 4-20mA electronic output is available for remote indication and SCADA integration
PROD_PDF_QUALITROL_KIT_930 | QUALITROL KIT-930 | PF_AUX_SENSOR | MET_POWER_SUPPLY | Voltage / frequency | 100 | 240 | 100 - 240 VAC, 50 / 60 Hz | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Field_Kit_for_930_Pressure_Monitor_5e0de6e3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 100 - 240 VAC, 50 / 60 Hz
PROD_PDF_QUALITROL_KIT_930 | QUALITROL KIT-930 | PF_AUX_SENSOR | MET_POWER_SUPPLY | DC output |  |  | 12 VDC | VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Field_Kit_for_930_Pressure_Monitor_5e0de6e3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 12 VDC
PROD_PDF_QUALITROL_KIT_930 | QUALITROL KIT-930 | PF_AUX_SENSOR | MET_PROTOCOL | Communication |  |  | MODBUS (remote) and USB (local) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Field_Kit_for_930_Pressure_Monitor_5e0de6e3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: MODBUS (remote) and USB (local)
PROD_PDF_QUALITROL_KIT_930 | QUALITROL KIT-930 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Operating temperature | -40 | 80 | -40 °C to 80 °C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Field_Kit_for_930_Pressure_Monitor_5e0de6e3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: -40 °C to 80 °C*
PROD_PDF_QUALITROL_KIT_930 | QUALITROL KIT-930 | PF_AUX_SENSOR | MET_HUMIDITY | Relative humidity |  | 90 | > 90 % | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Field_Kit_for_930_Pressure_Monitor_5e0de6e3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Relative humidity > 90 %
PROD_PDF_QUALITROL_KIT_930 | QUALITROL KIT-930 | PF_AUX_SENSOR | MET_HUMIDITY | Humidity range | 2 | 100 | RH 2% to 100% | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Field_Kit_for_930_Pressure_Monitor_5e0de6e3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: RH 2% to 100%
PROD_PDF_QUALITROL_KIT_930 | QUALITROL KIT-930 | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Enclosure protection |  |  | IP55 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Field_Kit_for_930_Pressure_Monitor_5e0de6e3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Enclosure protection IP55
PROD_PDF_QUALITROL_KIT_930 | QUALITROL KIT-930 | PF_AUX_SENSOR | MET_VIBRATION | Vibration |  |  | 50/60 Hz @ .004" displacement | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Field_Kit_for_930_Pressure_Monitor_5e0de6e3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 50/60 Hz @ .004” displacement
PROD_PDF_QUALITROL_KIT_930 | QUALITROL KIT-930 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Relay |  |  | Relay – 4A, 30 VDC, normally closed | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Field_Kit_for_930_Pressure_Monitor_5e0de6e3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Relay – 4A, 30 VDC, normally closed
PROD_PDF_QUALITROL_KIT_930 | QUALITROL KIT-930 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Solenoid valve / pressure switch |  |  | Normally open, approximately 0.5 inch H2O to close | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Field_Kit_for_930_Pressure_Monitor_5e0de6e3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Normally open, approximately 0.5 inch H2O to close
PROD_PDF_QUALITROL_505_ITM | Qualitrol 505 ITM | PF_TR_TEMP | MET_POWER_SUPPLY | Power supply type |  |  | Universal; 90 to 264 VAC; 47-63 Hz, 40-290 VDC | V AC/DC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_505_88332a90.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Universal; 90 to 264 watts VAC; 47-63 Hz, 40-290 VDC
PROD_PDF_QUALITROL_505_ITM | Qualitrol 505 ITM | PF_TR_TEMP | MET_SENSOR_COUNT | Input modules |  |  | Up to 4 input modules, 2 fixed, 2 configurable | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_505_88332a90.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Accepts up to 4 input modules, 2 fixed, 2 configurable
PROD_PDF_QUALITROL_505_ITM | Qualitrol 505 ITM | PF_TR_TEMP | MET_SENSOR_TYPE | RTD type |  |  | 10 ohm copper & 100 ohm platinum | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_505_88332a90.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: 10 ohm copper & 100 ohm platinum
PROD_PDF_QUALITROL_505_ITM | Qualitrol 505 ITM | PF_TR_TEMP | MET_OIL_TEMPERATURE | RTD measurement range | -40 | 120 | -40°C to 120°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_505_88332a90.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: -40°F to 248°F range (-40°C to 120°C)
PROD_PDF_QUALITROL_505_ITM | Qualitrol 505 ITM | PF_TR_TEMP | MET_CONTACT_TYPE | Output relays |  |  | 4 programmable, 1 system status, 1 heater; Form C, 10 amps | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_505_88332a90.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: 4 programmable, 1 system status, 1 relay for heater control
PROD_PDF_QUALITROL_505_ITM | Qualitrol 505 ITM | PF_TR_TEMP | MET_NETWORK | Communication ports |  |  | RS232, RS485 4-wire optically isolated, USB type B | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_505_88332a90.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: RS485 port 1 port, 4-wire optically isolated for digital protocols
PROD_PDF_QUALITROL_505_ITM | Qualitrol 505 ITM | PF_TR_TEMP | MET_PROTOCOL | Protocols |  |  | DNP 3.0 level 3 slave, Modbus RTU, ASCII | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_505_88332a90.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: DNP 3.0 level 3 slave, Modbus RTU, ASCII
PROD_PDF_QUALITROL_505_ITM | Qualitrol 505 ITM | PF_TR_TEMP | MET_AMBIENT_TEMP | Operating temperature | -40 | 72 | -40°C to +72°C (-60°C with heater) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_505_88332a90.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: -40°F to 161.6°F (-40°C to + 72°C)(-60 °C when a heater is used)
PROD_PDF_QUALITROL_505_ITM | Qualitrol 505 ITM | PF_TR_TEMP | MET_HUMIDITY | Humidity | 5 | 90 | 5% to 90% non-condensing | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_505_88332a90.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Humidity 5% to 90% non-condensing
PROD_PDF_QUALITROL_505_ITM | Qualitrol 505 ITM | PF_TR_TEMP | MET_ENCLOSURE_RATING | Mounting options |  |  | Weatherproof enclosure; panel mount; 19 inch rack mount | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_505_88332a90.pdf (page 8) | Datasheet-sourced (Step 0b). Evidence: Weatherproof enclosure Panel mount 19" rack mount
PROD_PDF_QUALITROL_507_ITM | Qualitrol 507 ITM | PF_TR_TEMP | MET_SENSOR_COUNT | Fiber optic inputs |  | 16 | Up to 16 Fiber Optic inputs | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_507_1210b08e.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Up to four flexible modular inputs and 16 Fiber Optic inputs
PROD_PDF_QUALITROL_507_ITM | Qualitrol 507 ITM | PF_TR_TEMP | MET_SENSOR_TYPE | Fiber optic temperature probe |  |  | GaAs fiber optic temp probe CAB-699 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_507_1210b08e.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Fiber optic temp probe CAB-699
PROD_PDF_QUALITROL_507_ITM | Qualitrol 507 ITM | PF_TR_TEMP | MET_WINDING_TEMP | Direct winding temperature accuracy |  |  | ±1°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_507_1210b08e.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Accuracy of ±1˚C
PROD_PDF_QUALITROL_507_ITM | Qualitrol 507 ITM | PF_TR_TEMP | MET_PROTOCOL | Communication protocols |  |  | DNP 3.0, MODBUS | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_507_1210b08e.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Protocols (DNP 3.0, MODBUS)
PROD_PDF_QUALITROL_507_ITM | Qualitrol 507 ITM | PF_TR_TEMP | MET_NETWORK | Digital communication interface |  |  | RS 485, RS 232; secure WiFi | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_507_1210b08e.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Digital communication (RS 485, RS 232)
PROD_PDF_QUALITROL_507_ITM | Qualitrol 507 ITM | PF_TR_TEMP | MET_DFR_FUNCTIONS | SCADA outputs |  |  | 0-1mA or 4-20mA | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_507_1210b08e.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: SCADA outputs (0-1mA or 4-20mA)
PROD_PDF_QUALITROL_507_ITM | Qualitrol 507 ITM | PF_TR_TEMP | MET_OIL_TEMPERATURE | Transformer temperature via RTD |  |  | RTD temperature measurements | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_507_1210b08e.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Provides transformer temperature measurements
PROD_PDF_QUALITROL_506_VTM | Qualitrol 506 VTM | PF_TR_TEMP | MET_PROTOCOL | Communication protocols |  |  | DNP or Modbus | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_507_1210b08e.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: we transmit the health of the transformer via DNP or Modbus
PROD_PDF_QUALITROL_506_VTM | Qualitrol 506 VTM | PF_TR_TEMP | MET_NETWORK | Communication interface |  |  | RS485 or RS232; fixed or secure WiFi | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_507_1210b08e.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Through RS485 or RS232
PROD_PDF_QUALITROL_506_VTM | Qualitrol 506 VTM | PF_TR_TEMP | MET_CONTACT_TYPE | Monitored inputs |  |  | Pressure, level and temperature inputs | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_507_1210b08e.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: inputs from pressure, level and temperature to monitored
PROD_PDF_QUALITROL_509_ITM | QUALITROL 509 ITM | PF_TR_TEMP | MET_POWER_SUPPLY | Power supply | 90 | 264 | Universal; 90 to 264 VAC; 47-63 Hz, 40-290 VDC | V AC/DC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_509_369c448e.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Universal; 90 to 264 watts VAC; 47-63 Hz, 40-290 VDC
PROD_PDF_QUALITROL_509_ITM | QUALITROL 509 ITM | PF_TR_TEMP | MET_SENSOR_COUNT | Number of input modules |  | 8 | Up to 8 input modules | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_509_369c448e.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Accepts up to 8 input modules of various, configurable types
PROD_PDF_QUALITROL_509_ITM | QUALITROL 509 ITM | PF_TR_TEMP | MET_SENSOR_TYPE | RTD type |  |  | 10 ohm copper & 100 ohm platinum | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_509_369c448e.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: 10 ohm copper & 100 ohm platinum
PROD_PDF_QUALITROL_509_ITM | QUALITROL 509 ITM | PF_TR_TEMP | MET_OIL_TEMPERATURE | RTD temperature range | -40 | 120 | -40°C to 120°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_509_369c448e.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: -40°F to 248°F range (-40°C to 120°C)
PROD_PDF_QUALITROL_509_ITM | QUALITROL 509 ITM | PF_TR_TEMP | MET_WINDING_TEMP | Winding temperature measurement |  |  | Direct and calculated winding temperature, up to 3 windings | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_509_369c448e.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Monitoring up to 3 windings
PROD_PDF_QUALITROL_509_ITM | QUALITROL 509 ITM | PF_TR_TEMP | MET_CONTACT_TYPE | Output relays |  |  | 8 programmable, 1 system status, 1 heater; Form C, 10 amps | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_509_369c448e.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: 8 programmable, 1 system status, 1 relay for heater control
PROD_PDF_QUALITROL_509_ITM | QUALITROL 509 ITM | PF_TR_TEMP | MET_NETWORK | Communications interfaces |  |  | RS232, RS485 4-wire isolated, fiber optic ST, USB, Ethernet | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_509_369c448e.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: RS485 port 1 port, 4-wire optically isolated for digital protocols
PROD_PDF_QUALITROL_509_ITM | QUALITROL 509 ITM | PF_TR_TEMP | MET_PROTOCOL | Protocols |  |  | DNP 3.0 level 1 slave, Modbus RTU, ASCII, IEC 61850, IEC 60870 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_509_369c448e.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: DNP 3.0 level 1 slave, Modbus RTU, ASCII, IEC 61850, IEC 60870
PROD_PDF_QUALITROL_509_ITM | QUALITROL 509 ITM | PF_TR_TEMP | MET_AMBIENT_TEMP | Operating temperature | -40 | 72 | -40°C to +72°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_509_369c448e.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Operating temperature -40°F to 161.6°F (-40°C to +72°C)
PROD_PDF_QUALITROL_509_ITM | QUALITROL 509 ITM | PF_TR_TEMP | MET_HUMIDITY | Humidity | 5 | 90 | 5% to 90% non-condensing | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_509_369c448e.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Humidity 5% to 90% non-condensing
PROD_PDF_QUALITROL_509_ITM | QUALITROL 509 ITM | PF_TR_TEMP | MET_ENCLOSURE_RATING | Mounting/enclosure options |  |  | Weatherproof enclosure, panel mount, 19 inch rack mount | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_509_369c448e.pdf (page 8) | Datasheet-sourced (Step 0b). Evidence: Weatherproof enclosure; Panel mount; 19" rack mount
PROD_PDF_QUALITROL_LPRD | QUALITROL LPRD | PF_AUX_SENSOR | MET_CONTACT_TYPE | Alarm switch contacts |  |  | Up to two alarm switches (with 4 contacts), SPDT or DPDT, latching or momentary | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/LPRD_Large_Pressure_Relief_Devices_72428d97.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: with up to two alarm switches (with 4 contacts)
PROD_PDF_QUALITROL_LPRD | QUALITROL LPRD | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Electrical connection rating |  |  | IP66, PG-13.5 cable entry, max. 2.5 mm2 wire (14 AWG) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/LPRD_Large_Pressure_Relief_Devices_72428d97.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: IP66, PG-13.5 cable entry, max. 2.5 mm 2-strand wire
PROD_PDF_QUALITROL_LPRD | QUALITROL LPRD | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Ambient operating temperature | -40 | 80 | -40°C to +80°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/LPRD_Large_Pressure_Relief_Devices_72428d97.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: -40°F to +176°F (-40°C to +80°C)
PROD_PDF_QUALITROL_LPRD | QUALITROL LPRD | PF_AUX_SENSOR | MET_OIL_TEMPERATURE | Oil operating temperature | -20 | 100 | -20°C to +100°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/LPRD_Large_Pressure_Relief_Devices_72428d97.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Oil operating -4°F to +212°F (-20°C to +100°C)
PROD_PDF_QUALITROL_LPRD | QUALITROL LPRD | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Electrical operating temperature | -25 | 85 | -25°C to +85°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/LPRD_Large_Pressure_Relief_Devices_72428d97.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Operating temperature -13°F to +185°F (-25°C to +85°C)
PROD_PDF_QUALITROL_LPRD | QUALITROL LPRD | PF_AUX_SENSOR | MET_POWER_SUPPLY | Switch rating |  |  | ½ A @ 125 VDC; ¼ A @ 250 VDC non-inductive | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/LPRD_Large_Pressure_Relief_Devices_72428d97.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: ½ A @ 125 VDC non-inductive
PROD_PDF_QUALITROL_LPRD | QUALITROL LPRD | PF_AUX_SENSOR | MET_POWER_RATING | Transformer rating application range | 300 | 10000 | 300 KVA to 10,000 KVA and above | kVA |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/LPRD_Large_Pressure_Relief_Devices_72428d97.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: in use on transformers rated as low as 300 KVA
PROD_PDF_NEOPTIX_T1_PROBE | Neoptix T1 Probe | PF_TR_TEMP | MET_SENSOR_TYPE | Sensor technology |  |  | GaAs 0.4 mm crystal, fiber optic | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Neoptix_T1_Fiber_Optic_Temperature_Probe_cf61e6a9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Probe sensitive area: GaAs 0.4 mm crystal, contact technology
PROD_PDF_NEOPTIX_T1_PROBE | Neoptix T1 Probe | PF_TR_TEMP | MET_AMBIENT_TEMP | Temperature range | -270 | 250 | -270 to +250 ºC | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Neoptix_T1_Fiber_Optic_Temperature_Probe_cf61e6a9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Temperature range: -270 to +250 º C
PROD_PDF_QUALITROL_NEOPTIX_T2_PROBE_T2S | Qualitrol Neoptix T2 Probe (T2S) | PF_TR_TEMP | MET_WINDING_TEMP | Measurement range | -80 | 250 | -80 to 250 °C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Neoptix_T2_Transformer_Temperature_Probe_7024aafc.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Measurement range -80 to 250 oC
PROD_PDF_QUALITROL_NEOPTIX_T2_PROBE_T2S | Qualitrol Neoptix T2 Probe (T2S) | PF_TR_TEMP | MET_SENSOR_TYPE | Probe sensor material |  |  | Gallium Arsenide (GaAs), 300 µ O.D. sensitive area | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Neoptix_T2_Transformer_Temperature_Probe_7024aafc.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Probe sensor Gallium Arsenide. Contact measurement with sensitive area of 300 µ
PROD_PDF_QUALITROL_NEOPTIX_T2_PROBE_T2S | Qualitrol Neoptix T2 Probe (T2S) | PF_TR_TEMP | MET_PD_LEVEL | Partial discharge |  |  | < 5 pC | pC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Neoptix_T2_Transformer_Temperature_Probe_7024aafc.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Partial discharge < 5 pC
PROD_PDF_QUALITROL_NEOPTIX_T2_PROBE_T2S | Qualitrol Neoptix T2 Probe (T2S) | PF_TR_TEMP | MET_SENSOR_TYPE | Connector type |  |  | Telecom multimode ST connector | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Neoptix_T2_Transformer_Temperature_Probe_7024aafc.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Connector type Telecom multimode ST connector
PROD_PDF_NOMAD_DIRECT | NOMAD-Direct | PF_TR_TEMP | MET_SENSOR_COUNT | Number of Channels |  |  | 2 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/NOMAD-Direct_Fiber-Optic_Temperature_Monitor_d7b954be.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Number of Channels 2
PROD_PDF_NOMAD_DIRECT | NOMAD-Direct | PF_TR_TEMP | MET_WINDING_TEMP | Calibrated Temperature Range | -20 | 150 | -20 °C to 150 °C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/NOMAD-Direct_Fiber-Optic_Temperature_Monitor_d7b954be.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Calibrated Temperature Range -20 °C to 150 °C
PROD_PDF_NOMAD_DIRECT | NOMAD-Direct | PF_TR_TEMP | MET_SENSOR_TYPE | Probe Compatibility |  |  | All Qualitrol Neoptix probes (T1 and T2) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/NOMAD-Direct_Fiber-Optic_Temperature_Monitor_d7b954be.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Probe Compatibility All Qualitrol Neoptix probes (T1 and T2)
PROD_PDF_NOMAD_DIRECT | NOMAD-Direct | PF_TR_TEMP | MET_AMBIENT_TEMP | Operating Temperature | 0 | 45 | 0 °C to 45 °C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/NOMAD-Direct_Fiber-Optic_Temperature_Monitor_d7b954be.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Operating Temperature 0 °C to 45 °C
PROD_PDF_NOMAD_DIRECT | NOMAD-Direct | PF_TR_TEMP | MET_HUMIDITY | Humidity |  | 95 | Up to 95% non-condensing | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/NOMAD-Direct_Fiber-Optic_Temperature_Monitor_d7b954be.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Humidity Up to 95% non-condensing
PROD_PDF_NOMAD_DIRECT | NOMAD-Direct | PF_TR_TEMP | MET_ENCLOSURE_RATING | Pollution Degree |  |  | PD2, indoor use only | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/NOMAD-Direct_Fiber-Optic_Temperature_Monitor_d7b954be.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Unit = PD2, indoor use only
PROD_PDF_NOMAD_DIRECT | NOMAD-Direct | PF_TR_TEMP | MET_POWER_SUPPLY | Charging Voltage |  |  | 5 VDC | VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/NOMAD-Direct_Fiber-Optic_Temperature_Monitor_d7b954be.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Charging Voltage 5 VDC
PROD_PDF_NOMAD_DIRECT | NOMAD-Direct | PF_TR_TEMP | MET_NETWORK | Charging Port Type |  |  | USB Type-C | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/NOMAD-Direct_Fiber-Optic_Temperature_Monitor_d7b954be.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Charging Port Type USB Type-C
PROD_PDF_NOMAD_DIRECT | NOMAD-Direct | PF_TR_TEMP | MET_POWER_SUPPLY | Internal Battery Type |  |  | Lithium-Ion rechargeable battery | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/NOMAD-Direct_Fiber-Optic_Temperature_Monitor_d7b954be.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Lithium-Ion rechargeable battery
PROD_PDF_QUALITROL_QHS393 | Qualitrol QHS393 | PF_AUX_SENSOR | MET_MOISTURE_OIL | Water activity measurement range | 0 | 1 | 0 - 1 aw | aw |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Oil_and_Moisture_Temperature_Sensor_acc1b1e0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Measurement range: 0 - 1 aw
PROD_PDF_QUALITROL_QHS393 | Qualitrol QHS393 | PF_AUX_SENSOR | MET_MOISTURE_OIL | Water activity accuracy |  |  | ±0.015 aw (0 - 0.9 aw) | aw |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Oil_and_Moisture_Temperature_Sensor_acc1b1e0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Accuracy at 20°C: ±0.015 a (0 - 0.9 a)w w
PROD_PDF_QUALITROL_QHS393 | Qualitrol QHS393 | PF_AUX_SENSOR | MET_OIL_TEMPERATURE | Temperature measurement range | -40 | 125 | -40 - +125 °C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Oil_and_Moisture_Temperature_Sensor_acc1b1e0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Measurement range: -40 - +125 °C
PROD_PDF_QUALITROL_QHS393 | Qualitrol QHS393 | PF_AUX_SENSOR | MET_OIL_TEMPERATURE | Temperature accuracy |  |  | ±0.2 °C at 20°C in oil | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Oil_and_Moisture_Temperature_Sensor_acc1b1e0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Accuracy at 20 °C in oil: ±0.2 °C
PROD_PDF_QUALITROL_QHS393 | Qualitrol QHS393 | PF_AUX_SENSOR | MET_OIL_TEMPERATURE | Oil temperature operating range | -40 | 125 | -40 - 125 °C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Oil_and_Moisture_Temperature_Sensor_acc1b1e0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Oil temperature: -40 - 125 °C
PROD_PDF_QUALITROL_QHS393 | Qualitrol QHS393 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Ambient temperature | -40 | 80 | -40 - 80 °C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Oil_and_Moisture_Temperature_Sensor_acc1b1e0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient temperature: -40 - 80 °C
PROD_PDF_QUALITROL_QHS393 | Qualitrol QHS393 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Storage temperature | -40 | 80 | -40 - 80 °C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Oil_and_Moisture_Temperature_Sensor_acc1b1e0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Storage temperature: -40 - 80 °C
PROD_PDF_QUALITROL_QHS393 | Qualitrol QHS393 | PF_AUX_SENSOR | MET_POWER_SUPPLY | Supply voltage | 12 | 36 | 12 - 36 V DC | V DC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Oil_and_Moisture_Temperature_Sensor_acc1b1e0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Supply voltage: 12 - 36 V DC
PROD_PDF_QUALITROL_QHS393 | Qualitrol QHS393 | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Housing / protection rating |  |  | Stainless steel 1.4404 or 316L / IP65 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Oil_and_Moisture_Temperature_Sensor_acc1b1e0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Housing / protection rating: Stainless steel ... IP65
PROD_PDF_QUALITROL_QHS393 | Qualitrol QHS393 | PF_AUX_SENSOR | MET_PROTOCOL | Digital output |  |  | Modbus RTU via RS485 interface | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Oil_and_Moisture_Temperature_Sensor_acc1b1e0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Digital output: Modbus RTU via RS485 interface
PROD_PDF_QUALITROL_QHS393 | Qualitrol QHS393 | PF_AUX_SENSOR | MET_NETWORK | Analogue outputs |  |  | 2 x 4-20 mA, max load < 500 Ohm | mA |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Oil_and_Moisture_Temperature_Sensor_acc1b1e0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 2 x analogue outputs: 4 - 20 mA Max. load < 500 Ohm
PROD_PDF_QUALITROL_QHS393 | Qualitrol QHS393 | PF_AUX_SENSOR | MET_SENSOR_TYPE | Sensor element |  |  | Capacitive sensor element | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Oil_and_Moisture_Temperature_Sensor_acc1b1e0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Capacitive sensor element
PROD_PDF_QUALITROL_OFT_OFT_1 | QUALITROL OFT (OFT-1) | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Operating temperature | -80 | 200 | -80°C to 200°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Optical_Feedthrough_(OFT)_65c52d3a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Operating temperature -80°C to 200° C
PROD_PDF_QUALITROL_OFT_OFT_1 | QUALITROL OFT (OFT-1) | PF_AUX_SENSOR | MET_SENSOR_TYPE | Connector type |  |  | ST type connectors, both ends | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Optical_Feedthrough_(OFT)_65c52d3a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: ST CONNECTOR BOTH ENDS
PROD_PDF_QUALITROL_KIT_013 | QUALITROL KIT-013 | PF_AUX_SENSOR | MET_POWER_SUPPLY | Power supply |  |  | Batteries / integrated power supply | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Rapid_Pressure_Rise_Relay_Test_Kit_7cf61c38.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Pressure gauge, power supply, test lights and operation buttons
PROD_PDF_QUALITROL_STB000_SERIES | Qualitrol STB000 Series | PF_AUX_SENSOR | MET_PROTOCOL | Communication options |  |  | RJ45, RS-485 Modbus and alarm relays | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Smart_Transformer_Breathers_b5c5ff49.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: including RJ45, RS-485 Modbus and alarm relays
PROD_PDF_QUALITROL_STB000_SERIES | Qualitrol STB000 Series | PF_AUX_SENSOR | MET_NETWORK | Local USB port |  |  | local USB port inside control box | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Smart_Transformer_Breathers_b5c5ff49.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: A local USB port inside the control box provides for local reading
PROD_PDF_QUALITROL_STB000_SERIES | Qualitrol STB000 Series | PF_AUX_SENSOR | MET_CONTACT_TYPE | Alarm and status relays |  |  | Alarm and Status relays, failsafe or non-failsafe | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Smart_Transformer_Breathers_b5c5ff49.pdf (page 6) | Datasheet-sourced (Step 0b). Evidence: Alarm and Status relays can be set for failsafe or non-failsafe operation
PROD_PDF_QUALITROL_STB000_SERIES | Qualitrol STB000 Series | PF_AUX_SENSOR | MET_MOISTURE_OIL | Regeneration threshold based on RH/PPM |  |  | Relative Humidity (RH), Parts Per Million (PPM) or time | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Smart_Transformer_Breathers_b5c5ff49.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: based on % Relative Humidity (RH), Parts Per Million (PPM) or time
PROD_PDF_QUALITROL_STB000_SERIES | Qualitrol STB000 Series | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Enclosure rating |  |  | IP enclosure ratings | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Smart_Transformer_Breathers_b5c5ff49.pdf (page 11) | Datasheet-sourced (Step 0b). Evidence: IP enclosure ratings
PROD_PDF_QUALITROL_STB000_SERIES | Qualitrol STB000 Series | PF_AUX_SENSOR | MET_ALARM_THRESHOLD | Alarming and failure detection |  |  | Alarming and failure detection capability | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Smart_Transformer_Breathers_b5c5ff49.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Alarming and failure detection capability no need to rely on human interaction
PROD_PDF_QUALITROL_STB000_SERIES | Qualitrol STB000 Series | PF_AUX_SENSOR | MET_POWER_RATING | Recommended transformer rating |  |  | medium/large transformers - 30kV & above | kV |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Smart_Transformer_Breathers_b5c5ff49.pdf (page 8) | Datasheet-sourced (Step 0b). Evidence: Recommended for use on medium/large transformers - 30kV & above
PROD_PDF_QUALITROL_STB000_SERIES | Qualitrol STB000 Series | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Datalogged internal temperatures |  |  | tracks internal temperatures | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Smart_Transformer_Breathers_b5c5ff49.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Relative Humidity levels and internal temperatures
PROD_PDF_QUALITROL_OFFSHORE_XTREME_SMART_TRANSFORMER_BREATHER | Qualitrol Offshore Xtreme Smart Transformer Breather | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Hardened enclosure |  |  | 316 grade stainless steel; IP enclosure ratings | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Smart_Transformer_Breathers_b5c5ff49.pdf (page 11) | Datasheet-sourced (Step 0b). Evidence: Extensive use of 316 grade stainless steel metal components
PROD_PDF_T_GUARD_LINK_REVB | T/Guard-Link RevB | PF_TR_TEMP | MET_SENSOR_COUNT | Number of channels | 2 | 8 | 2, 4, 6 or 8; up to 32 modules cascaded (256 channels) | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TGuard_Link_RevB_Fiber-Optic_Hot-Spot_Monitor_b37a6673.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 2, 4, 6 or 8. With Modbus, up to 32 modules
PROD_PDF_T_GUARD_LINK_REVB | T/Guard-Link RevB | PF_TR_TEMP | MET_SENSOR_TYPE | Probe compatibility |  |  | Compatible with ALL Neoptix probes (GaAs); also Nortech Fibronic | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TGuard_Link_RevB_Fiber-Optic_Hot-Spot_Monitor_b37a6673.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Compatible with ALL Neoptix probes
PROD_PDF_T_GUARD_LINK_REVB | T/Guard-Link RevB | PF_TR_TEMP | MET_WINDING_TEMP | Measurement range | -80 | 250 | -80 to +250 °C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TGuard_Link_RevB_Fiber-Optic_Hot-Spot_Monitor_b37a6673.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Measurement range -80 to +250 oC
PROD_PDF_T_GUARD_LINK_REVB | T/Guard-Link RevB | PF_TR_TEMP | MET_WINDING_TEMP | Accuracy |  |  | +/- 1 °C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TGuard_Link_RevB_Fiber-Optic_Hot-Spot_Monitor_b37a6673.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: Accuracy of +/- 1 ˚C
PROD_PDF_T_GUARD_LINK_REVB | T/Guard-Link RevB | PF_TR_TEMP | MET_WINDING_TEMP | Resolution reading |  |  | 0.1 °C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TGuard_Link_RevB_Fiber-Optic_Hot-Spot_Monitor_b37a6673.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Resolution reading 0.1 °C
PROD_PDF_T_GUARD_LINK_REVB | T/Guard-Link RevB | PF_TR_TEMP | MET_PROTOCOL | Communication protocols |  |  | ASCII (Neoptix commands) or serial Modbus RTU | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TGuard_Link_RevB_Fiber-Optic_Hot-Spot_Monitor_b37a6673.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: ASCII (Neoptix commands) or serial Modbus RTU
PROD_PDF_T_GUARD_LINK_REVB | T/Guard-Link RevB | PF_TR_TEMP | MET_NETWORK | Communication hardware |  |  | Optically isolated RS-485 and analog outputs, half or full duplex | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TGuard_Link_RevB_Fiber-Optic_Hot-Spot_Monitor_b37a6673.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Optically isolated RS-485 and analog outputs
PROD_PDF_T_GUARD_LINK_REVB | T/Guard-Link RevB | PF_TR_TEMP | MET_POWER_SUPPLY | Power requirement | 20 | 28 | 24 VDC nominal (20-28 VDC acceptable) | VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TGuard_Link_RevB_Fiber-Optic_Hot-Spot_Monitor_b37a6673.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 24 VDC nominal (20-28 VDC acceptable)
PROD_PDF_T_GUARD_LINK_REVB | T/Guard-Link RevB | PF_TR_TEMP | MET_AMBIENT_TEMP | Operating temperature | -40 | 72 | -40 to +72 °C, 5-90% humidity non-condensing | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TGuard_Link_RevB_Fiber-Optic_Hot-Spot_Monitor_b37a6673.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Operating temperature -40 to +72 °C, 5-90 % humidity
PROD_PDF_T_GUARD_LINK_REVB | T/Guard-Link RevB | PF_TR_TEMP | MET_HUMIDITY | Operating humidity | 5 | 90 | 5-90 % non-condensing | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TGuard_Link_RevB_Fiber-Optic_Hot-Spot_Monitor_b37a6673.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 5-90 % humidity, non-condensing
PROD_PDF_T_GUARD_LINK_REVB | T/Guard-Link RevB | PF_TR_TEMP | MET_ENCLOSURE_RATING | Form factor |  |  | Solid cast aluminum enclosure, must be protected from rain, dust | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TGuard_Link_RevB_Fiber-Optic_Hot-Spot_Monitor_b37a6673.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Solid aluminum enclosure, mounting brackets at each corner
PROD_PDF_T_GUARD_LINK_REVB | T/Guard-Link RevB | PF_TR_TEMP | MET_VIBRATION | Vibrations |  |  | 60/120 Hz @ 0.1 mm displacement | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TGuard_Link_RevB_Fiber-Optic_Hot-Spot_Monitor_b37a6673.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Vibrations 60/120 Hz @ 0.1 mm displacement
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | MET_DGA_GAS_SPECIES | Measured Gas |  |  | Hydrogen (H2) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM1_ad935707.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Solid-state H2 sensor immersed directly in the oil
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | MET_DGA_GAS_COUNT | Number of Gases |  |  | 1 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM1_ad935707.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: The TM1 is selective for hydrogen exclusively
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | MET_ALARM_THRESHOLD | Hydrogen Range | 20 | 10000 | 20 – 10,000 ppm | ppm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM1_ad935707.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 20 – 10,000 ppm; Lower Detection Limit 20 ppm
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | MET_MOISTURE_OIL | Moisture-in-Oil Range | 0 | 100 | 0-100% RS, ±5% | %RS |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM1_ad935707.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Moisture-in-Oil ±5% 0-100% RS
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | MET_OIL_TEMPERATURE | Oil Temperature Measurement | -40 | 120 | -40°C to +120°C, ±2°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM1_ad935707.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Oil Temperature ±2°C -40°C to +120°C
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | MET_AMBIENT_TEMP | Operating Temperature | -50 | 55 | -50°C to +55°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM1_ad935707.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Operating Temperature -50°C to +55°C
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | MET_ENCLOSURE_RATING | Enclosure Rating |  |  | NEMA 4X, IP66 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM1_ad935707.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Enclosure Rating NEMA 4X, IP66
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | MET_POWER_SUPPLY | Input Power | 100 | 240 | 100-240 VAC, 50/60 Hz, 0.8 A max | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM1_ad935707.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 100 - 240 VAC 50/60 Hz 0.8 A max.
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | MET_PROTOCOL | Supported Protocols |  |  | DNP3 and Modbus | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM1_ad935707.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Supported Protocols DNP3 and Modbus
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | MET_NETWORK | Communications Interfaces |  |  | RS232/485, USB 2.0, three analog 4-20 mA outputs | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM1_ad935707.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: RS232 / 485, USB 2.0, Three (3) analog 4-20 mA outputs
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | MET_CONTACT_TYPE | Alarm Relays |  |  | Three programmable DGA relays; two power/service relays | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM1_ad935707.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Three (3) programmable alarm relays; Two (2) alarm relays
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_DGA_GAS_COUNT | Number of fault gases measured |  |  | 3 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: correlates 3 fault gases (acetylene, ethylene, and methane)
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_DGA_GAS_SPECIES | DGA gas species |  |  | Methane (CH4), Ethylene (C2H4), Acetylene (C2H2) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Methane (CH4) Ethylene (C2H4) Acetylene (C2H2)
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_DGA_GAS_SPECIES | Methane range and accuracy | 5 | 7000 | ±5% or ±5 ppm, <1% repeatability | ppm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: ±5% or ±5 ppm <1% 5-7,000 ppm
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_DGA_GAS_SPECIES | Ethylene range and accuracy | 3 | 5000 | ±5% or ±3 ppm, <1% repeatability | ppm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: ±5% or ±3 ppm <1% 3-5,000 ppm
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_DGA_GAS_SPECIES | Acetylene range and accuracy | 1 | 3000 | ±5% or ±1 ppm, <2% repeatability | ppm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: ±5% or ±1 ppm <2% 1-3,000 ppm
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_MOISTURE_OIL | Moisture-in-Oil | 0 | 100 | ±2% accuracy, 0-100% RS | % RS |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: ±2% 0-100% RS
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_OIL_TEMPERATURE | Oil Temperature | -40 | 180 | 0.1°C typically, -40°C to +180°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 0.1°C (typically) -40°C to +180°C
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_SENSOR_TYPE | DGA Method |  |  | Laboratory Grade Gas Chromatography | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: DGA Method: Laboratory Grade Gas Chromatography
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_ANALOG_CHANNELS | Analog inputs |  |  | Three (3) analog 4 to 20 mA inputs | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Three (3) analog 4 to 20 mA inputs, ambient temperature sensor included
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_ALARM_THRESHOLD | Alarm relays |  |  | Two individually programmable relays | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Alarms Two individually programmable relays
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_CONTACT_TYPE | Relay contact rating |  |  | 50 VDC or 240 VAC @ 3 A max; normally open or normally closed | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: relay contacts operate as normally open or normally closed
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_PROTOCOL | Supported protocols |  |  | TCP/IP, DNP3, Modbus RTU, ASCII, OPC and IEC 61850 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: TCP/IP , DNP3, Modbus RTU, ASCII, OPC and IEC 61850
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_NETWORK | Communication interfaces |  |  | RS-232, RS-485, Ethernet Fiber (100Base-FX), Ethernet Copper (10/100Base-TX), Cellular modem, Wireless Radio, V.92 modem | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: RS-232, RS-485, Ethernet Fiber (100Base-FX), Cellular modem
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_POWER_SUPPLY | Input power |  |  | 115 VAC or 230 VAC ±15%, 50/60 Hz | V AC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 115 VAC or 230 VAC ±15% 50/60 Hz
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_AMBIENT_TEMP | Operating Temperature | -50 | 55 | -50°C to +55°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Operating T emperature -50°C to +55°C
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_HUMIDITY | Operating Humidity | 5 | 95 | 5% to 95% RH, non-condensing | %RH |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 5% to 95% RH, non-condensing
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_ENCLOSURE_RATING | Enclosure Rating |  |  | NEMA 4X, IP66 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: NEMA 4X, IP66
PROD_PDF_QUALITROL_XPRD | Qualitrol XPRD | PF_AUX_SENSOR | MET_CONTACT_TYPE | Electrical switch rating (standard) |  |  | 10 A @ 125/250 VAC (standard) | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/XPRD_Extra_Large_Pressure_Relief_Device_cf600595.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch options 10 A@ 125/250 VAC (standard)
PROD_PDF_QUALITROL_XPRD | Qualitrol XPRD | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch DC rating |  |  | 0.5 A @ 125 VDC; 0.25 A @ 250 VDC non-inductive; High DC 10 A @ 125 VDC | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/XPRD_Extra_Large_Pressure_Relief_Device_cf600595.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 0.5 A @ 125 VDC non-inductive
PROD_PDF_QUALITROL_XPRD | Qualitrol XPRD | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Ambient operating temperature | -40 | 80 | -40°C to 80°C (tank fluid at 30°C) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/XPRD_Extra_Large_Pressure_Relief_Device_cf600595.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Ambient operating temperature -40°C to 80°C
PROD_PDF_QUALITROL_XPRD | Qualitrol XPRD | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Switch enclosure rating |  |  | IP54 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/XPRD_Extra_Large_Pressure_Relief_Device_cf600595.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch enclosure Meets IP54 requirements
PROD_PDF_IDM_PMU_9 | IDM+PMU 9 | PF_PMU | MET_ANALOG_CHANNELS | Analog channels |  |  | 9 | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 9 analog and 32 digital channels (IDM+PMU 9)
PROD_PDF_IDM_PMU_9 | IDM+PMU 9 | PF_PMU | MET_DFR_FUNCTIONS | Digital channels |  |  | 32 | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 9 analog and 32 digital channels (IDM+PMU 9)
PROD_PDF_IDM_PMU_9 | IDM+PMU 9 | PF_PMU | MET_FEEDER_COUNT | Circuit capacity |  |  | one full circuit or two circuits | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: configured to monitor one full circuit ... or two circuits
PROD_PDF_IDM_PMU_9 | IDM+PMU 9 | PF_PMU | MET_POWER_SUPPLY | Power supply |  |  | 88 to 250 VAC, 88 to 300 VDC; option 35 to 65 VDC | V AC/DC |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 88 to 250 VAC, 88 to 300 VDC; option 35 to 65 VDC
PROD_PDF_IDM_PMU_9 | IDM+PMU 9 | PF_PMU | MET_POWER_RATING | Power (max load) |  |  | 40 VA | VA |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 40 VA (for IDM+PMU 9)
PROD_PDF_IDM_PMU_9 | IDM+PMU 9 | PF_PMU | MET_SAMPLING_RATE | Sample rate |  |  | 512 samples / cycle | samples/cycle |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 512 samples / cycle
PROD_PDF_IDM_PMU_9 | IDM+PMU 9 | PF_PMU | MET_REPORTING_RATE | Frame rate |  | 50 | up to 50 or 60 Hz | Hz |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Frame rates up to 50 or 60 Hz
PROD_PDF_IDM_PMU_9 | IDM+PMU 9 | PF_PMU | MET_TIME_SYNC | Clock synchronization |  |  | GPS module, IRIG-B (with 1pps), IRIG-J | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: synchronized by GPS module, IRIG-B (with 1pps), IRIG-J
PROD_PDF_IDM_PMU_9 | IDM+PMU 9 | PF_PMU | MET_GPS_SYNC_ACCURACY | Clock accuracy |  |  | 1µs when locked | µs |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 1µs when locked
PROD_PDF_IDM_PMU_9 | IDM+PMU 9 | PF_PMU | MET_NETWORK | Ethernet ports |  |  | 2 provided - RJ45 front, RJ45 (fibre option) rear | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 2 provided - RJ45 for local connection at the front
PROD_PDF_IDM_PMU_9 | IDM+PMU 9 | PF_PMU | MET_ENCLOSURE_RATING | Mounting |  |  | 3U, 19" rack mount | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 3U, 19” rack mount
PROD_PDF_IDM_PMU_9 | IDM+PMU 9 | PF_PMU | MET_AMBIENT_TEMP | Operating temperature | -5 | 50 | -5 to +50º C | °C |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Operating: -5 to +50º C [23 to 122º F]
PROD_PDF_IDM_PMU_9 | IDM+PMU 9 | PF_PMU | MET_ANALOG_CHANNELS | Accuracy |  |  | 1% TVE between 10% and 120% of nominal | % TVE |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Current: 1% TVE maintained between 10% and 120% of nominal
PROD_PDF_IDM_PMU_18 | IDM+PMU 18 | PF_PMU | MET_ANALOG_CHANNELS | Analog channels |  |  | 18 | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 18 analog and 32 digital channels (IDM+PMU 18)
PROD_PDF_IDM_PMU_18 | IDM+PMU 18 | PF_PMU | MET_DFR_FUNCTIONS | Digital channels |  |  | 32 | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 18 analog and 32 digital channels (IDM+PMU 18)
PROD_PDF_IDM_PMU_18 | IDM+PMU 18 | PF_PMU | MET_FEEDER_COUNT | Circuit capacity |  |  | three or five circuits | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: IDM+PMU 18 device can be configured to monitor three or five circuits
PROD_PDF_IDM_PMU_18 | IDM+PMU 18 | PF_PMU | MET_POWER_RATING | Power (max load) |  |  | 80 VA | VA |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 80 VA (for IDM+PMU 18 and IDM+PMU 36)
PROD_PDF_IDM_PMU_18 | IDM+PMU 18 | PF_PMU | MET_POWER_SUPPLY | Power supply |  |  | 88 to 250 VAC, 88 to 300 VDC; option 35 to 65 VDC | V AC/DC |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 88 to 250 VAC, 88 to 300 VDC; option 35 to 65 VDC
PROD_PDF_IDM_PMU_18 | IDM+PMU 18 | PF_PMU | MET_SAMPLING_RATE | Sample rate |  |  | 512 samples / cycle | samples/cycle |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 512 samples / cycle
PROD_PDF_IDM_PMU_18 | IDM+PMU 18 | PF_PMU | MET_REPORTING_RATE | Frame rate |  | 50 | up to 50 or 60 Hz | Hz |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Frame rates up to 50 or 60 Hz
PROD_PDF_IDM_PMU_18 | IDM+PMU 18 | PF_PMU | MET_TIME_SYNC | Clock synchronization |  |  | GPS module, IRIG-B (with 1pps), IRIG-J | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: synchronized by GPS module, IRIG-B (with 1pps), IRIG-J
PROD_PDF_IDM_PMU_18 | IDM+PMU 18 | PF_PMU | MET_NETWORK | Ethernet ports |  |  | 2 provided - RJ45 front, RJ45 (fibre option) rear | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 2 provided - RJ45 for local connection at the front
PROD_PDF_IDM_PMU_18 | IDM+PMU 18 | PF_PMU | MET_ENCLOSURE_RATING | Mounting |  |  | 6U, 19" rack mount | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 6U, 19” rack mount
PROD_PDF_IDM_PMU_18 | IDM+PMU 18 | PF_PMU | MET_AMBIENT_TEMP | Operating temperature | -5 | 50 | -5 to +50º C | °C |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Operating: -5 to +50º C [23 to 122º F]
PROD_PDF_IDM_PMU_36 | IDM+PMU 36 | PF_PMU | MET_ANALOG_CHANNELS | Analog channels |  |  | 36 | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 36 analog and 64 digital channels (IDM+PMU 36)
PROD_PDF_IDM_PMU_36 | IDM+PMU 36 | PF_PMU | MET_DFR_FUNCTIONS | Digital channels |  |  | 64 | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 36 analog and 64 digital channels (IDM+PMU 36)
PROD_PDF_IDM_PMU_36 | IDM+PMU 36 | PF_PMU | MET_FEEDER_COUNT | Circuit capacity |  | 10 | six or ten circuits | count |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: IDM+PMU 36 device can be configured to monitor six or ten circuits
PROD_PDF_IDM_PMU_36 | IDM+PMU 36 | PF_PMU | MET_POWER_RATING | Power (max load) |  |  | 80 VA | VA |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 80 VA (for IDM+PMU 18 and IDM+PMU 36)
PROD_PDF_IDM_PMU_36 | IDM+PMU 36 | PF_PMU | MET_POWER_SUPPLY | Power supply |  |  | 88 to 250 VAC, 88 to 300 VDC; option 35 to 65 VDC | V AC/DC |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 88 to 250 VAC, 88 to 300 VDC; option 35 to 65 VDC
PROD_PDF_IDM_PMU_36 | IDM+PMU 36 | PF_PMU | MET_SAMPLING_RATE | Sample rate |  |  | 512 samples / cycle | samples/cycle |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 512 samples / cycle
PROD_PDF_IDM_PMU_36 | IDM+PMU 36 | PF_PMU | MET_REPORTING_RATE | Frame rate |  | 50 | up to 50 or 60 Hz | Hz |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Frame rates up to 50 or 60 Hz
PROD_PDF_IDM_PMU_36 | IDM+PMU 36 | PF_PMU | MET_TIME_SYNC | Clock synchronization |  |  | GPS module, IRIG-B (with 1pps), IRIG-J | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: synchronized by GPS module, IRIG-B (with 1pps), IRIG-J
PROD_PDF_IDM_PMU_36 | IDM+PMU 36 | PF_PMU | MET_NETWORK | Ethernet ports |  |  | 4 provided - 2 x RJ45 front, 2 x RJ45 (fibre option) rear | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 4 provided - 2 x RJ45 for local connection at the front
PROD_PDF_IDM_PMU_36 | IDM+PMU 36 | PF_PMU | MET_ENCLOSURE_RATING | Mounting |  |  | 6U, 19" rack mount | text |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 6U, 19” rack mount
PROD_PDF_IDM_PMU_36 | IDM+PMU 36 | PF_PMU | MET_AMBIENT_TEMP | Operating temperature | -5 | 50 | -5 to +50º C | °C |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+PMU_7cb7c557.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Operating: -5 to +50º C [23 to 122º F]
PROD_PDF_QUALITROL_032_042_045_LARGE_OIL_LEVEL_INDICATOR | Qualitrol 032/042/045 Large Oil Level Indicator | PF_AUX_SENSOR | MET_SENSOR_COUNT | Number of switches |  | 3 | Up to 3 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/045_Liquid_Level_Gauge_09f522e9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Number of switches Up to 3
PROD_PDF_QUALITROL_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATOR | Qualitrol AKM 44712/34725 Large Oil Level Indicator | PF_AUX_SENSOR | MET_SENSOR_COUNT | Number of switches |  | 4 | 4 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/045_Liquid_Level_Gauge_09f522e9.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Number of switches 4
PROD_PDF_AKM_35600_47500 | AKM 35600 / 47500 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type |  |  | SPST or SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/146_PressureVacuum_Switch_ddef168f.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Switch type SPST or SPDT
PROD_PDF_AKM_35600_47500 | AKM 35600 / 47500 | PF_AUX_SENSOR | MET_SENSOR_COUNT | Number of switches available | 2 | 3 | 2 or 3 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/146_PressureVacuum_Switch_ddef168f.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Number of switches available 2 or 3
PROD_PDF_AKM_35600_47500 | AKM 35600 / 47500 | PF_AUX_SENSOR | MET_POWER_SUPPLY | Switch rating |  |  | 5 A @ 125 VAC, 3 A @ 250 VAC resistive | A/V |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/146_PressureVacuum_Switch_ddef168f.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Switch rating 5 A @ 125 VAC resistive
PROD_PDF_AKM_35600_47500 | AKM 35600 / 47500 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Std. operating temperatures | -40 | 80 | -40 to 176ºF (-40 to +80ºC) | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/146_PressureVacuum_Switch_ddef168f.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Std. operating temperatures -40 to 176ºF (-40 to +80ºC)
PROD_PDF_AKM_35600_47500 | AKM 35600 / 47500 | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Weatherproof case |  |  | IP55 standard | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/146_PressureVacuum_Switch_ddef168f.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: comes standard with a weather proof case (IP55)
PROD_PDF_AKM_35600_47500 | AKM 35600 / 47500 | PF_AUX_SENSOR | MET_TRIP_CLOSE_TIME | Reaction time |  | 15 | less than 15 milliseconds | ms |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/146_PressureVacuum_Switch_ddef168f.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: react in less than 15 milliseconds when pressure changes
PROD_PDF_QUALITROL_AKM_35600 | QUALITROL AKM 35600 | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Weather proof case |  |  | IP55 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/148_PressureVacuum_Switch_2a33e83a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: comes standard with a weather proof case (IP55)
PROD_PDF_QUALITROL_AKM_47500 | QUALITROL AKM 47500 | PF_AUX_SENSOR | MET_CONTACT_TYPE | Switch type |  |  | SPST or SPDT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/148_PressureVacuum_Switch_2a33e83a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Switch type SPST or SPDT
PROD_PDF_QUALITROL_AKM_47500 | QUALITROL AKM 47500 | PF_AUX_SENSOR | MET_SENSOR_COUNT | Number of switches available | 2 | 3 | 2 or 3 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/148_PressureVacuum_Switch_2a33e83a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Number of switches available 2 or 3
PROD_PDF_QUALITROL_AKM_47500 | QUALITROL AKM 47500 | PF_AUX_SENSOR | MET_AMBIENT_TEMP | Std. operating temperatures | -40 | 80 | -40 to 176ºF | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/148_PressureVacuum_Switch_2a33e83a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Std. operating temperatures -40 to 176ºF (-40 to +80ºC)
PROD_PDF_AKM_35600_47500 | AKM 35600 / 47500 | PF_AUX_SENSOR | MET_ENCLOSURE_RATING | Weather proof case |  |  | IP55 | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_47500_Pressure_Control_Switches_1068660c.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: AKM 35600 comes standard with a weather proof case (IP55)
PROD_PDF_AKM_38750_38920_38960 | AKM 38750/38920/38960 | PF_BREAKER | MET_INDICATION_ACCURACY | Indication accuracy |  |  | ±2% of max scale value | % |  |  | Preparation/Qualitrol Product/Breakers/SF6_Gas_Density_Gauges_0d311061.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Indication accuracy ± 2% of max scale value for fill pressure
PROD_PDF_AKM_38750_38920_38960 | AKM 38750/38920/38960 | PF_BREAKER | MET_INDICATION_ACCURACY | Switching accuracy |  |  | ±3% of max scale value | % |  |  | Preparation/Qualitrol Product/Breakers/SF6_Gas_Density_Gauges_0d311061.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switching accuracy ± 3% of max scale value for fill pressure
PROD_PDF_AKM_38750_38920_38960 | AKM 38750/38920/38960 | PF_BREAKER | MET_NUMBER_OF_SWITCHES | Number of switches | 0 | 3 | 0, 1, 2 or 3 | count |  |  | Preparation/Qualitrol Product/Breakers/SF6_Gas_Density_Gauges_0d311061.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Number of switches 0, 1, 2 or 3
PROD_PDF_AKM_38750_38920_38960 | AKM 38750/38920/38960 | PF_BREAKER | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 2000 VAC between switch contacts and ground for 60 seconds | V |  |  | Preparation/Qualitrol Product/Breakers/SF6_Gas_Density_Gauges_0d311061.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 2000 VAC between switch contacts and ground for 60 seconds
PROD_PDF_AKM_38750_38920_38960 | AKM 38750/38920/38960 | PF_BREAKER | MET_PROCESS_CONNECTION | Tank connection |  |  | M30 x 2 mm with O-ring seal (standard) | text |  |  | Preparation/Qualitrol Product/Breakers/SF6_Gas_Density_Gauges_0d311061.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: M 30 x 2 mm with O-ring seal is standard
PROD_PDF_QUALITROL_QPDM_SERIES | Qualitrol QPDM Series | PF_PD_TRANSFORMER | MET_FREQUENCY_BANDWIDTH | Frequency bandwidth | 300 | 2100 | 300 MHz to 2100 MHz with HDR card | MHz |  |  | Preparation/Qualitrol Product/Gas_Insulated_Switchgear/QPDM_Software_fad2476a.pdf (page 11) | Datasheet-sourced (Step 0b). Evidence: Frequency bandwidth 300 MHz to 2100 MHz with HDR card
PROD_PDF_IRIS_POWER_CAPACITIVE_AIR_GAP_SENSOR_CGS020210_CGP_02 | Iris Power Capacitive Air Gap Sensor CGS020210 (CGP-02) | PF_GEN_AIRGAP | MET_INDICATION_ACCURACY | Full Range Accuracy |  |  | ±3% | % |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Full Range Accuracy ±3%
PROD_PDF_IRIS_POWER_CAPACITIVE_AIR_GAP_SENSOR_CGS020310_CGP_03 | Iris Power Capacitive Air Gap Sensor CGS020310 (CGP-03) | PF_GEN_AIRGAP | MET_INDICATION_ACCURACY | Full Range Accuracy |  |  | ±3% | % |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Full Range Accuracy ±3%
PROD_PDF_IRIS_POWER_CAPACITIVE_AIR_GAP_SENSOR_CGS020410_CGP_04 | Iris Power Capacitive Air Gap Sensor CGS020410 (CGP-04) | PF_GEN_AIRGAP | MET_INDICATION_ACCURACY | Full Range Accuracy |  |  | ±5% | % |  |  | Preparation/Qualitrol Product/Generator_Solutions/Capacitive_Air_Gap_Sensor_d4fb14ac.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Full Range Accuracy ±5%
PROD_PDF_IRIS_POWER_EPOXY_MICA_CAPACITORS_EMC_80_PF | Iris Power Epoxy Mica Capacitors (EMC) 80 pF | PF_GEN_PD | MET_FREQUENCY_BANDWIDTH | Bandwidth into 50 ohms (3 dB) | 40 | 500 | 40 MHz to 500 MHz | MHz |  |  | Preparation/Qualitrol Product/Generator_Solutions/Epoxy_Mica_Capacitors_(EMC_Sensors)_8912f79b.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Bandwidth into 50 ohms (3 dB): 40 MHz to 500 MHz
PROD_PDF_IRIS_POWER_MDSP3 | Iris Power MDSP3 | PF_MOTOR | MET_WEIGHT | Weight |  |  | 0.4 kg (1 lb) | kg |  |  | Preparation/Qualitrol Product/Generator_Solutions/MDSP3_aee0c628.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Weight 0.4 kg (1 lb)
PROD_PDF_IRIS_POWER_PDA_IV | Iris Power PDA-IV | PF_GEN_PD | MET_FREQUENCY_BANDWIDTH | Frequency Bandwidth | 0.1 | 350 | 0.1 MHz - 350 MHz | MHz |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDA-IV_e8515c86.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Frequency Bandwidth 0.1 MHz - 350 MHz
PROD_PDF_IRIS_POWER_PDA_IV | Iris Power PDA-IV | PF_GEN_PD | MET_PHASE_WINDOWS | Phase Windows |  |  | 100 phase windows per cycle | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDA-IV_e8515c86.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Phase Windows 100 phase windows per cycle
PROD_PDF_IRIS_POWER_PDA_IV | Iris Power PDA-IV | PF_GEN_PD | MET_RESPONSE_TIME | Data Acquisition Time |  |  | 1s or 5s per magnitude window | s |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDA-IV_e8515c86.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Data Acquisition Time 1s or 5s per magnitude window
PROD_PDF_IRIS_POWER_PDTRACII_4208 | Iris Power PDTracII 4208 | PF_MOTOR | MET_FREQUENCY_BANDWIDTH | Frequency Bandwidth | 0.1 | 350 | 0.1 MHz - 350 MHz | MHz |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDTracII_08f5c95a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Frequency Bandwidth 0.1 MHz - 350 MHz
PROD_PDF_IRIS_POWER_PDTRACII_4208 | Iris Power PDTracII 4208 | PF_MOTOR | MET_PHASE_WINDOWS | Phase Windows |  |  | 24 phase windows per cycle | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/PDTracII_08f5c95a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 24 phase windows per cycle
PROD_PDF_IRIS_POWER_CORONA_PROBE_MODEL_PPM_97 | Iris Power Corona Probe Model PPM-97 | PF_GEN_PD | MET_FREQUENCY_BANDWIDTH | Bandwidth | 0.5 | 10 | 0.5 – 10 MHz | MHz |  |  | Preparation/Qualitrol Product/Generator_Solutions/PPM-97_Corona_Probe_9c7539d3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Bandwidth 0.5 – 10 MHz
PROD_PDF_IRIS_POWER_CORONA_PROBE_MODEL_PPM_97 | Iris Power Corona Probe Model PPM-97 | PF_GEN_PD | MET_WEIGHT | Weight (meter only) |  |  | 445 grams | grams |  |  | Preparation/Qualitrol Product/Generator_Solutions/PPM-97_Corona_Probe_9c7539d3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Weight (meter only) 445 grams
PROD_PDF_IRIS_POWER_CORONA_PROBE_MODEL_PPM_97 | Iris Power Corona Probe Model PPM-97 | PF_GEN_PD | MET_PROBE_LENGTH | Probe Length |  |  | 91cm | cm |  |  | Preparation/Qualitrol Product/Generator_Solutions/PPM-97_Corona_Probe_9c7539d3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Probe Length 91cm
PROD_PDF_QCM_PPDM | QCM-PPDM | PF_PD_TRANSFORMER | MET_POWER_CONSUMPTION | Power |  |  | 70 W | W |  |  | Preparation/Qualitrol Product/Generator_Solutions/QPPDM_2ca3bb9a.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: 70 W
PROD_PDF_QCM_PPDM | QCM-PPDM | PF_PD_TRANSFORMER | MET_STORAGE_TEMP | Storage temperature | -25 | 75 | -25ºC to +75ºC | °C |  |  | Preparation/Qualitrol Product/Generator_Solutions/QPPDM_2ca3bb9a.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: -25ºC to +75ºC
PROD_PDF_IRIS_POWER_RFAII_R | Iris Power RFAII-R | PF_GEN_AIRGAP | MET_POWER_CONSUMPTION | Power consumption |  |  | <100 W | W |  |  | Preparation/Qualitrol Product/Generator_Solutions/RFAII-R_c16db884.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Consumption: <100 W
PROD_PDF_IRIS_POWER_RFAII_S | Iris Power RFAII-S | PF_GEN_AIRGAP | MET_POWER_CONSUMPTION | Power consumption |  |  | <100 W | W |  |  | Preparation/Qualitrol Product/Generator_Solutions/RFAII-S_551dd1fa.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Consumption: <100 W
PROD_PDF_IRIS_POWER_STATOR_SLOT_COUPLERS_SSC | Iris Power Stator Slot Couplers (SSC) | PF_GEN_PD | MET_FREQUENCY_BANDWIDTH | Bandwidth | 10 | 1000 | 10-1000 MHz (3 dB cut-off) | MHz |  |  | Preparation/Qualitrol Product/Generator_Solutions/Stator_Slot_Couplers_(SSC)_bb887587.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 10-1000 MHz bandwidth (3 dB cut-off)
PROD_PDF_IRIS_POWER_TGA_B | Iris Power TGA-B | PF_GEN_PD | MET_FREQUENCY_BANDWIDTH | Frequency Bandwidth | 0.1 | 350 | 0.1 MHz - 350 MHz | MHz |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-B_b099cbd2.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Frequency Bandwidth 0.1 MHz - 350 MHz
PROD_PDF_IRIS_POWER_TGA_B | Iris Power TGA-B | PF_GEN_PD | MET_PHASE_WINDOWS | Phase Windows |  |  | 100 phase windows per cycle | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-B_b099cbd2.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 100 phase windows per cycle
PROD_PDF_IRIS_POWER_TGA_B | Iris Power TGA-B | PF_GEN_PD | MET_RESPONSE_TIME | Data Acquisition Time |  |  | 1s or 5s per magnitude window | s |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-B_b099cbd2.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 1s or 5s per magnitude window
PROD_PF_GEN_PD_02 | TGA-S | PF_GEN_PD | MET_FREQUENCY_BANDWIDTH | Frequency Bandwidth | 0.1 | 350 | 0.1 MHz - 350 MHz | MHz |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-S_c922447e.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Frequency Bandwidth 0.1 MHz - 350 MHz
PROD_PF_GEN_PD_02 | TGA-S | PF_GEN_PD | MET_PHASE_WINDOWS | Phase Windows |  |  | 100 phase windows per cycle | count |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-S_c922447e.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Phase Windows 100 phase windows per cycle
PROD_PF_GEN_PD_02 | TGA-S | PF_GEN_PD | MET_RESPONSE_TIME | Data Acquisition Time |  |  | 1s or 5s per magnitude window | s |  |  | Preparation/Qualitrol Product/Generator_Solutions/TGA-S_c922447e.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Data Acquisition Time 1s or 5s per magnitude window
PROD_PF_DGA_03 | Serveron TM8 | PF_DGA | MET_OPERATING_PRESSURE | Oil inlet pressure | 0 | 45 | 0 to 45 psi (0 to 3 bar) | psi |  |  | Preparation/Qualitrol Product/Software_Solutions/TMView_8bc233a4.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Oil Inlet Pressure 0 to 45 psi (0 to 3 bar)
PROD_PF_DFR_01 | IDM+ | PF_DFR | MET_INDICATION_ACCURACY | Input accuracy |  |  | 0.1% voltage and 0.1% current full scale | % |  |  | Preparation/Qualitrol Product/The_Power_Grid/IDM+_22da82f9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 0.1% voltage and 0.1% current - full scale
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | MET_INDICATION_ACCURACY | DC channel angle error |  |  | Error ≤ 0.1° | degree |  |  | Preparation/Qualitrol Product/The_Power_Grid/Informa_PQ_17eb70e4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Error 0.1°
PROD_PF_PQ_06 | INFORMA PMD-A | PF_PQ | MET_FREQUENCY_BANDWIDTH | Analog bandwidth | 25 | 4600 | 25 to 4600 Hz ± 0.5 dB | Hz |  |  | Preparation/Qualitrol Product/The_Power_Grid/Informa_PQ_17eb70e4.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Bandwidth 25 to 4600 Hz ± 0.5 dB
PROD_PDF_QUALITROL_015_VERTICAL_OIL_LEVEL_INDICATOR | Qualitrol 015 Vertical Oil Level Indicator | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | Vertical orientation only (top mount) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/015_Vertical_Oil_Level_Indicator_fb43241e.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Mounting Vertical orientation only (top mount)
PROD_PDF_QUALITROL_015_VERTICAL_OIL_LEVEL_INDICATOR | Qualitrol 015 Vertical Oil Level Indicator | PF_AUX_SENSOR | MET_PROCESS_CONNECTION | Tank connection |  |  | ISO 228/1-G1.5A male thread | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/015_Vertical_Oil_Level_Indicator_fb43241e.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Tank connection ISO 228/1-G1.5A male thread
PROD_PDF_QUALITROL_020_030_AKM_46969 | Qualitrol 020/030 & AKM 46969 | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | Flange mount, various sizes available | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/020_Small_Oil_Level_Indicator_00ef7115.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Flange mount, various sizes available
PROD_PDF_QUALITROL_020_030_AKM_46969 | Qualitrol 020/030 & AKM 46969 | PF_AUX_SENSOR | MET_DIAL_RANGE | Standard dial ranges |  |  | High - Low, Min - Max | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/020_Small_Oil_Level_Indicator_00ef7115.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Standard dial ranges High - Low, Min - Max
PROD_PDF_QUALITROL_020_030_AKM_46969 | Qualitrol 020/030 & AKM 46969 | PF_AUX_SENSOR | MET_DIAL_DIAMETER | Dial diameter |  |  | 2.00" or 3.00" (50.8 mm or 76.2 mm) | in/mm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/020_Small_Oil_Level_Indicator_00ef7115.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Dial diameter 2.00" or 3.00" (50.8 mm or 76.2 mm)
PROD_PDF_QUALITROL_020_030_AKM_46969 | Qualitrol 020/030 & AKM 46969 | PF_AUX_SENSOR | MET_CASE_MATERIAL | Case material |  |  | Die-cast aluminum or brass, thermosetting powder coat finish | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/020_Small_Oil_Level_Indicator_00ef7115.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Case Die-cast aluminum or brass, thermosetting powder coat finish
PROD_PDF_QUALITROL_020_030_AKM_46969 | Qualitrol 020/030 & AKM 46969 | PF_AUX_SENSOR | MET_FLOAT_MECHANISM | Float material |  |  | Nitrophyl | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/020_Small_Oil_Level_Indicator_00ef7115.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Float Nitrophyl
PROD_PDF_QUALITROL_029_VERTICAL_OIL_LEVEL_INDICATOR | Qualitrol 029 Vertical Oil Level Indicator | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | Weld on flange | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/029_Subway_Oil_Level_Indicator_8f7dd70b.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Mounting Weld on flange
PROD_PDF_QUALITROL_029_VERTICAL_OIL_LEVEL_INDICATOR | Qualitrol 029 Vertical Oil Level Indicator | PF_AUX_SENSOR | MET_DIAL_DIAMETER | Dial diameter |  |  | 3.00 in (76.2 mm) | in/mm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/029_Subway_Oil_Level_Indicator_8f7dd70b.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Dial diameter 3.00" (76.2 mm)
PROD_PDF_QUALITROL_029_VERTICAL_OIL_LEVEL_INDICATOR | Qualitrol 029 Vertical Oil Level Indicator | PF_AUX_SENSOR | MET_CASE_MATERIAL | Case Material |  |  | Brass or stainless steel with thermosetting powder coat finish | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/029_Subway_Oil_Level_Indicator_8f7dd70b.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Case Brass or stainless steel, ASA #70 light grey
PROD_PDF_QUALITROL_029_VERTICAL_OIL_LEVEL_INDICATOR | Qualitrol 029 Vertical Oil Level Indicator | PF_AUX_SENSOR | MET_FLOAT_MECHANISM | Float Material |  |  | Nitrophyl | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/029_Subway_Oil_Level_Indicator_8f7dd70b.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Float Nitrophyl
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_SWITCH_RATING_DC | Switch rating (DC) 032/042/045 |  |  | 1/2A @ 125 VDC, 1/4A @ 250 VDC resistive | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 1/2A @ 125 VDC, resistive
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_SWITCH_RATING_DC | Switch rating (DC) 44712/34725 |  |  | 0.30A @ 125 VDC, resistive | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 0.30A @ 125 VDC, resistive
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_DIELECTRIC_STRENGTH | Dielectric strength (032/042/045) |  |  | 1,500 VAC for 60 seconds | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 1,500 VAC for 60 seconds
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_DIELECTRIC_STRENGTH | Dielectric strength (44712/34725) |  |  | 2,000 VAC for 60 seconds | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 2,000 VAC for 60 seconds
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_MAX_LOAD | Max load |  |  | 600Ω | ohm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Max load 600Ω
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting (032/042/045) |  |  | Flange mount, various sizes available | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Mounting Flange mount, various sizes available
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting (44712/34725) |  |  | M50 thread mount | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting M50 thread mount
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_DIAL_DIAMETER | Dial diameter (032/042/045) |  |  | 5.5" (140mm) | in/mm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Dial diameter 5.5" (140mm)
PROD_PDF_QUALITROL_032_042_045_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATORS | QUALITROL 032/042/045 & AKM 44712/34725 Large Oil Level Indicators | PF_AUX_SENSOR | MET_DIAL_DIAMETER | Dial diameter (44712/34725) |  |  | 5.9" (150mm) or 9.8" (250mm) | in/mm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/032_Lever_Driven_Liquid_Level_Gauge_e614075a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dial diameter 5.9" (150 mm) or 9.8" (250 mm)
PROD_PDF_QUALITROL_035_LIQUID_LEVEL_CONTROL_GAUGE | QUALITROL 035 Liquid Level Control Gauge | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | Flange mount | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/035_Flange_Mounted_Liquid_Level_Gauge_3a00eded.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting Flange mount
PROD_PDF_QUALITROL_035_LIQUID_LEVEL_CONTROL_GAUGE | QUALITROL 035 Liquid Level Control Gauge | PF_AUX_SENSOR | MET_FLOAT_MECHANISM | Float mechanism |  |  | Lever | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/035_Flange_Mounted_Liquid_Level_Gauge_3a00eded.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Float mechanism Lever
PROD_PDF_QUALITROL_035_LIQUID_LEVEL_CONTROL_GAUGE | QUALITROL 035 Liquid Level Control Gauge | PF_AUX_SENSOR | MET_DIAL_DIAMETER | Dial diameter |  |  | 3.75" (95.25 mm) | in/mm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/035_Flange_Mounted_Liquid_Level_Gauge_3a00eded.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dial diameter 3.75" (95.25 mm)
PROD_PDF_QUALITROL_035_LIQUID_LEVEL_CONTROL_GAUGE | QUALITROL 035 Liquid Level Control Gauge | PF_AUX_SENSOR | MET_CASE_MATERIAL | Case material |  |  | Die-cast aluminum, ASA #70 light gray thermosetting powder coat finish | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/035_Flange_Mounted_Liquid_Level_Gauge_3a00eded.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Case Die-cast aluminum, ASA #70 light gray thermosetting
PROD_PDF_QUALITROL_035_LIQUID_LEVEL_CONTROL_GAUGE | QUALITROL 035 Liquid Level Control Gauge | PF_AUX_SENSOR | MET_SWITCH_RATING_AC | Switch rating (AC) |  |  | 10A @ 125, 250, 480 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/035_Flange_Mounted_Liquid_Level_Gauge_3a00eded.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 10A @ 125, 250, 480 VAC
PROD_PDF_QUALITROL_035_LIQUID_LEVEL_CONTROL_GAUGE | QUALITROL 035 Liquid Level Control Gauge | PF_AUX_SENSOR | MET_SWITCH_RATING_DC | Switch rating (DC) |  |  | ½A @ 125 VDC resistive, ¼A @ 250 VDC resistive | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/035_Flange_Mounted_Liquid_Level_Gauge_3a00eded.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: ½A @ 125 VDC, resistive ¼A @ 250 VDC, resistive
PROD_PDF_QUALITROL_035_LIQUID_LEVEL_CONTROL_GAUGE | QUALITROL 035 Liquid Level Control Gauge | PF_AUX_SENSOR | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 1,500 VAC for 60 seconds | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/035_Flange_Mounted_Liquid_Level_Gauge_3a00eded.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dielectric strength 1,500 VAC for 60 seconds
PROD_PDF_QUALITROL_035_LIQUID_LEVEL_CONTROL_GAUGE | QUALITROL 035 Liquid Level Control Gauge | PF_AUX_SENSOR | MET_PROCESS_CONNECTION | Connection type |  |  | Flying leads (standard), quick connectors, sealed-weatherproof connectors, terminal box | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/035_Flange_Mounted_Liquid_Level_Gauge_3a00eded.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Flying leads (standard), quick connectors, sealed-weatherproof connectors, terminal box
PROD_PDF_QUALITROL_038_GAS_ACCUMULATION_INDICATOR | QUALITROL 038 Gas Accumulation Indicator | PF_AUX_SENSOR | MET_SWITCH_RATING_AC | Switch rating (AC) |  |  | 15 amp @ 125, 250 & 480 VAC, resistive | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/038_Gas_Accumulation_Indicator_a3362790.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 15 amp @ 125, 250 & 480 VAC, resistive
PROD_PDF_QUALITROL_038_GAS_ACCUMULATION_INDICATOR | QUALITROL 038 Gas Accumulation Indicator | PF_AUX_SENSOR | MET_SWITCH_RATING_DC | Switch rating (DC) |  |  | ½ Amp @ 125 VDC; ¼ Amp @ 250 VDC resistive | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/038_Gas_Accumulation_Indicator_a3362790.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (DC) ½ Amp @ 125 VDC - resistive
PROD_PDF_QUALITROL_038_GAS_ACCUMULATION_INDICATOR | QUALITROL 038 Gas Accumulation Indicator | PF_AUX_SENSOR | MET_INDICATION_ACCURACY | Switching accuracy |  |  | ±2ºC | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/038_Gas_Accumulation_Indicator_a3362790.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switching accuracy ±2ºC
PROD_PDF_QUALITROL_038_GAS_ACCUMULATION_INDICATOR | QUALITROL 038 Gas Accumulation Indicator | PF_AUX_SENSOR | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 1500 VAC for one minute | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/038_Gas_Accumulation_Indicator_a3362790.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dielectric strength 1500 VAC for one minute
PROD_PDF_QUALITROL_038_GAS_ACCUMULATION_INDICATOR | QUALITROL 038 Gas Accumulation Indicator | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | 2 - 5/8 X 1.5" LG bolts or studs on 4.25" centers | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/038_Gas_Accumulation_Indicator_a3362790.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 5/8 X 1.5” LG bolts or studs on 4.25” centers
PROD_PDF_QUALITROL_038_GAS_ACCUMULATION_INDICATOR | QUALITROL 038 Gas Accumulation Indicator | PF_AUX_SENSOR | MET_WEIGHT | Weight |  |  | 11.00 lbs (5 kg) | lbs/kg |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/038_Gas_Accumulation_Indicator_a3362790.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Weight 11.00 lbs (5 kg)
PROD_PDF_QUALITROL_038_GAS_ACCUMULATION_INDICATOR | QUALITROL 038 Gas Accumulation Indicator | PF_AUX_SENSOR | MET_DIAL_DIAMETER | Dimensions |  |  | Dial diameter 6.00" (152 mm) | mm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/038_Gas_Accumulation_Indicator_a3362790.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dimensions Dial diameter 6.00” (152 mm)
PROD_PDF_QUALITROL_038_GAS_ACCUMULATION_INDICATOR | QUALITROL 038 Gas Accumulation Indicator | PF_AUX_SENSOR | MET_PROCESS_CONNECTION | Tank connection |  |  | 3/8"-18 NPT (standard) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/038_Gas_Accumulation_Indicator_a3362790.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Tank connection 3/8”-18 NPT (standard)
PROD_PDF_QUALITROL_032_042_045 | QUALITROL 032/042/045 | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | Flange mount, various sizes available | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Mounting Flange mount, various sizes available
PROD_PDF_QUALITROL_032_042_045 | QUALITROL 032/042/045 | PF_AUX_SENSOR | MET_FLOAT_MECHANISM | Float mechanism |  |  | Gear (042 and 045 series) or lever (032 series) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Gear (042 and 045 series) or lever (032 series)
PROD_PDF_QUALITROL_032_042_045 | QUALITROL 032/042/045 | PF_AUX_SENSOR | MET_DIAL_DIAMETER | Dial diameter |  |  | 5.5" (140mm) | in/mm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Dial diameter 5.5" (140mm)
PROD_PDF_QUALITROL_032_042_045 | QUALITROL 032/042/045 | PF_AUX_SENSOR | MET_NUMBER_OF_SWITCHES | Number of switches |  | 3 | Up to 3 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Number of switches Up to 3
PROD_PDF_QUALITROL_032_042_045 | QUALITROL 032/042/045 | PF_AUX_SENSOR | MET_SWITCH_RATING_AC | Switch rating (AC) |  |  | 10A @ 125, 250, 480 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 10A @ 125, 250, 480 VAC
PROD_PDF_QUALITROL_032_042_045 | QUALITROL 032/042/045 | PF_AUX_SENSOR | MET_SWITCH_RATING_DC | Switch rating (DC) |  |  | 1/2A @ 125 VDC, 1/4A @ 250 VDC resistive | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 1/2A @ 125 VDC, resistive 1/4A @ 250 VDC
PROD_PDF_QUALITROL_032_042_045 | QUALITROL 032/042/045 | PF_AUX_SENSOR | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 1,500 VAC for 60 seconds | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Dielectric strength 1,500 VAC for 60 seconds
PROD_PDF_QUALITROL_032_042_045 | QUALITROL 032/042/045 | PF_AUX_SENSOR | MET_ANALOG_OUTPUT | SCADA output signal |  |  | 4-20mA or 0-1mA (Only with 039 Remote Enclosure) | mA |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 4 - 20mA or 0 - 1mA (Only with 039 Remote Enclosure)
PROD_PDF_QUALITROL_032_042_045 | QUALITROL 032/042/045 | PF_AUX_SENSOR | MET_MAX_LOAD | Max load |  |  | 600Ω | ohm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Max load 600Ω
PROD_PDF_QUALITROL_AKM_44712_34725 | QUALITROL AKM 44712/34725 | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | M50 thread mount | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting M50 thread mount
PROD_PDF_QUALITROL_AKM_44712_34725 | QUALITROL AKM 44712/34725 | PF_AUX_SENSOR | MET_FLOAT_MECHANISM | Float mechanism |  |  | Gear (34725) or lever (44712) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Float mechanism Gear (34725) or lever (44712)
PROD_PDF_QUALITROL_AKM_44712_34725 | QUALITROL AKM 44712/34725 | PF_AUX_SENSOR | MET_DIAL_DIAMETER | Dial diameter |  |  | 5.9" (150 mm) or 9.8" (250 mm) | in/mm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dial diameter 5.9" (150 mm) or 9.8" (250 mm)
PROD_PDF_QUALITROL_AKM_44712_34725 | QUALITROL AKM 44712/34725 | PF_AUX_SENSOR | MET_NUMBER_OF_SWITCHES | Number of switches |  | 4 | 4 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Number of switches 4
PROD_PDF_QUALITROL_AKM_44712_34725 | QUALITROL AKM 44712/34725 | PF_AUX_SENSOR | MET_SWITCH_RATING_AC | Switch rating (AC) |  |  | 5A @ 250 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 5A @ 250 VAC
PROD_PDF_QUALITROL_AKM_44712_34725 | QUALITROL AKM 44712/34725 | PF_AUX_SENSOR | MET_SWITCH_RATING_DC | Switch rating (DC) |  |  | 0.30A @ 125 VDC, resistive | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (DC) 0.30A @ 125 VDC, resistive
PROD_PDF_QUALITROL_AKM_44712_34725 | QUALITROL AKM 44712/34725 | PF_AUX_SENSOR | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 2,000 VAC for 60 seconds | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dielectric strength 2,000 VAC for 60 seconds
PROD_PDF_QUALITROL_AKM_44712_34725 | QUALITROL AKM 44712/34725 | PF_AUX_SENSOR | MET_ANALOG_OUTPUT | SCADA output signal |  |  | 4-20 mA | mA |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Output signal 4 - 20 mA
PROD_PDF_QUALITROL_AKM_44712_34725 | QUALITROL AKM 44712/34725 | PF_AUX_SENSOR | MET_MAX_LOAD | Max load |  |  | 600Ω | ohm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/042_Gear_Driven_Liquid_Level_Gauge_48f8f967.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Max load 600Ω
PROD_PDF_QUALITROL_049 | Qualitrol 049 | PF_AUX_SENSOR | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 2000 VAC between individual switch contacts and ground for 60s | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/049_Vertical_Oil_Level_Indicator_b0a06108.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 2000 VAC between individual switch contacts and ground for 60s
PROD_PDF_QUALITROL_049 | Qualitrol 049 | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | R-1½ Male Thread (DIN 259), vertical installation only | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/049_Vertical_Oil_Level_Indicator_b0a06108.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: R-1½ Male Thread (DIN 259), vertical installation only
PROD_PDF_QUALITROL_049 | Qualitrol 049 | PF_AUX_SENSOR | MET_FLOAT_MECHANISM | Float material |  |  | Nitrophyl | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/049_Vertical_Oil_Level_Indicator_b0a06108.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Float material Nitrophyl
PROD_PDF_QUALITROL_050 | Qualitrol 050 | PF_AUX_SENSOR | MET_INDICATION_ACCURACY | Accuracy |  |  | ±3% of full scale | % |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/050_PressureVacuum_Gauge_and_Bleeders_940edfee.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Accuracy of ±3% of full scale provides reliable readings
PROD_PDF_QUALITROL_050 | Qualitrol 050 | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | ¼-18 NPT thread mount | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/050_PressureVacuum_Gauge_and_Bleeders_940edfee.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: ¼-18 NPT thread mount (centered on back of indicator)
PROD_PDF_QUALITROL_070_SERIES_PRESSURE_VACUUM_BLEEDER | QUALITROL 070 Series Pressure-Vacuum Bleeder | PF_AUX_SENSOR | MET_DIAL_RANGE | Dial range (070 series) |  |  | -5 to 5 PSI, -10 to 10 PSI | PSI |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/070_PressureVacuum_Gauge_and_Bleeders_36edcc50.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dial range (070 series) -5 to 5 PSI, -10 to 10 PSI
PROD_PDF_QUALITROL_070_SERIES_PRESSURE_VACUUM_BLEEDER | QUALITROL 070 Series Pressure-Vacuum Bleeder | PF_AUX_SENSOR | MET_REPEATABILITY | Repeatability |  |  | ±0.5 PSI | PSI |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/070_PressureVacuum_Gauge_and_Bleeders_36edcc50.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Repeatability ±0.5 PSI
PROD_PDF_QUALITROL_070_SERIES_PRESSURE_VACUUM_BLEEDER | QUALITROL 070 Series Pressure-Vacuum Bleeder | PF_AUX_SENSOR | MET_DIAL_DIAMETER | Dial diameter (070 series) |  |  | 3.5" (89 mm) | mm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/070_PressureVacuum_Gauge_and_Bleeders_36edcc50.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dial diameter (070 series) 3.5" (89 mm)
PROD_PDF_QUALITROL_070_SERIES_PRESSURE_VACUUM_BLEEDER | QUALITROL 070 Series Pressure-Vacuum Bleeder | PF_AUX_SENSOR | MET_PROCESS_CONNECTION | Tank connection |  |  | 1/4-18 NPT, 1/8-27 NPT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/070_PressureVacuum_Gauge_and_Bleeders_36edcc50.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Tank connection 1/4-18 NPT, 1/8-27 NPT
PROD_PDF_QUALITROL_351_SERIES_PRESSURE_VACUUM_BLEEDER | QUALITROL 351 Series Pressure-Vacuum Bleeder | PF_AUX_SENSOR | MET_REPEATABILITY | Repeatability |  |  | ±0.5 PSI | PSI |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/070_PressureVacuum_Gauge_and_Bleeders_36edcc50.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Repeatability ±0.5 PSI
PROD_PDF_QUALITROL_351_SERIES_PRESSURE_VACUUM_BLEEDER | QUALITROL 351 Series Pressure-Vacuum Bleeder | PF_AUX_SENSOR | MET_PROCESS_CONNECTION | Tank connection |  |  | 1/4-18 NPT, 1/8-27 NPT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/070_PressureVacuum_Gauge_and_Bleeders_36edcc50.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Tank connection 1/4-18 NPT, 1/8-27 NPT
PROD_PDF_QUALITROL_092_FLOW_INDICATORS | QUALITROL 092 Flow Indicators | PF_AUX_SENSOR | MET_OPERATING_PRESSURE | Operating pressure |  | 35 | 35 psi maximum | psi |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/092_Flow_Gauge_13c5e971.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Operating pressure 35 psi maximum
PROD_PDF_QUALITROL_092_FLOW_INDICATORS | QUALITROL 092 Flow Indicators | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | Bolted flange | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/092_Flow_Gauge_13c5e971.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting Bolted flange
PROD_PDF_QUALITROL_092_FLOW_INDICATORS | QUALITROL 092 Flow Indicators | PF_AUX_SENSOR | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 1500 VAC for one minute | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/092_Flow_Gauge_13c5e971.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dielectric strength 1500 VAC for one minute
PROD_PDF_QUALITROL_104_TR6000_REMOTE_MOUNT_THERMOMETERS | QUALITROL 104/TR6000 Remote Mount Thermometers | PF_TR_TEMP | MET_SWITCH_RATING_AC | Switch rating (AC) |  |  | 10A and 1/3 HP @ 120-240 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/104TR6000_Remote_Temperature_Indicator_5d6da65e.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 10A and 1/3 HP @ 120-240 VAC
PROD_PDF_QUALITROL_104_TR6000_REMOTE_MOUNT_THERMOMETERS | QUALITROL 104/TR6000 Remote Mount Thermometers | PF_TR_TEMP | MET_SWITCH_RATING_DC | Switch rating (DC) |  |  | 0.50A at 125 VDC resistive; 0.25A at 250 VDC resistive | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/104TR6000_Remote_Temperature_Indicator_5d6da65e.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: 0.50A at 125 VDC resistive 0.25A at 250 VDC resistive
PROD_PDF_QUALITROL_104_TR6000_REMOTE_MOUNT_THERMOMETERS | QUALITROL 104/TR6000 Remote Mount Thermometers | PF_TR_TEMP | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 1500 VAC, optional 2000 VAC, 50/60 Hz | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/104TR6000_Remote_Temperature_Indicator_5d6da65e.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Dielectric strength 1500 VAC, 50/60 Hz, Optional 2000 VAC
PROD_PDF_QUALITROL_104_TR6000_REMOTE_MOUNT_THERMOMETERS | QUALITROL 104/TR6000 Remote Mount Thermometers | PF_TR_TEMP | MET_DIAL_DIAMETER | Dial diameter |  |  | 6" (152.4 mm) | mm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/104TR6000_Remote_Temperature_Indicator_5d6da65e.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Dial diameter 6" (152.4 mm)
PROD_PDF_QUALITROL_105_REMOTE_MOUNT_THERMOMETER | QUALITROL 105 Remote Mount Thermometer | PF_TR_TEMP | MET_INDICATION_ACCURACY | Accuracy |  |  | +/- 2% of dial range | % of dial range |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/105_Remote_Mount_Thermometer_b568f343.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Accuracy +/- 2% of dial range
PROD_PDF_QUALITROL_105_REMOTE_MOUNT_THERMOMETER | QUALITROL 105 Remote Mount Thermometer | PF_TR_TEMP | MET_SWITCH_RATING_AC | Switch rating (AC) |  |  | 10A @ 125, 250 & 480 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/105_Remote_Mount_Thermometer_b568f343.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 10A @ 125, 250 & 480 VAC
PROD_PDF_QUALITROL_105_REMOTE_MOUNT_THERMOMETER | QUALITROL 105 Remote Mount Thermometer | PF_TR_TEMP | MET_SWITCH_RATING_DC | Switch rating (DC) |  |  | 1/4A @ 250 VDC; 1/2A @ 125 VDC; 1.5A @ 48 VDC - resistive | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/105_Remote_Mount_Thermometer_b568f343.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (DC) 1/4A @ 250 VDC - resistive
PROD_PDF_QUALITROL_105_REMOTE_MOUNT_THERMOMETER | QUALITROL 105 Remote Mount Thermometer | PF_TR_TEMP | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 1500 VAC for one minute | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/105_Remote_Mount_Thermometer_b568f343.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dielectric strength 1500 VAC for one minute
PROD_PDF_QUALITROL_105_REMOTE_MOUNT_THERMOMETER | QUALITROL 105 Remote Mount Thermometer | PF_TR_TEMP | MET_MOUNTING_TYPE | Mounting |  |  | Vertical (back plate or panel mounting) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/105_Remote_Mount_Thermometer_b568f343.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting Vertical (back plate or panel mounting)
PROD_PDF_QUALITROL_120 | Qualitrol 120 | PF_TR_TEMP | MET_SWITCH_CONTACT_RATING | Switch ratings |  |  | 10 Amp @ 125,250 & 480 VAC; 1/2A @125VDC | A/V |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/120_Bourdon_Tube_Thermometer_a5e8092f.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 10 Amp. @ 125, 250 & 480 VAC
PROD_PDF_QUALITROL_120 | Qualitrol 120 | PF_TR_TEMP | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 1500 VAC 50/60 Hz standard, 2000 VAC optional | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/120_Bourdon_Tube_Thermometer_a5e8092f.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dielectric strength 1500 VAC, 50/60 Hz (standard)
PROD_PDF_QUALITROL_120 | Qualitrol 120 | PF_TR_TEMP | MET_MOUNTING_TYPE | Mounting style |  |  | Center back thread | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/120_Bourdon_Tube_Thermometer_a5e8092f.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting style Center back thread
PROD_PDF_QUALITROL_120 | Qualitrol 120 | PF_TR_TEMP | MET_PROCESS_CONNECTION | Connection type |  |  | Qualitrol, ANSI, or MIL quick-disconnect; terminal box, cable, flying-leads | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/120_Bourdon_Tube_Thermometer_a5e8092f.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Qualitrol, ANSI, or MIL quick-disconnect; terminal box
PROD_PDF_QUALITROL_130 | QUALITROL 130 | PF_TR_TEMP | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 2000 VAC for one minute | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/130_Thermal_Plate_0dbe066d.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Dielectric strength 2000 VAC for one minute
PROD_PDF_QUALITROL_130 | QUALITROL 130 | PF_TR_TEMP | MET_MOUNTING_TYPE | Mounting |  |  | Top or side mount | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/130_Thermal_Plate_0dbe066d.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Mounting Top or side mount
PROD_PDF_QUALITROL_THERMAL_PLATE | QUALITROL Thermal Plate | PF_TR_TEMP | MET_MOUNTING_TYPE | Mounting |  |  | Side mount (flange) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/130_Thermal_Plate_0dbe066d.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: Mounting Side mount (flange)
PROD_PDF_QUALITROL_141 | Qualitrol 141 | PF_AUX_SENSOR | MET_NUMBER_OF_SWITCHES | Number of switches available |  |  | 2 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Number of switches available 2
PROD_PDF_QUALITROL_141 | Qualitrol 141 | PF_AUX_SENSOR | MET_SWITCH_CONTACT_RATING | Switch rating (AC) |  |  | 15 A @ 125, 250, 480 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 15 A @ 125, 250, 480 VAC
PROD_PDF_QUALITROL_141 | Qualitrol 141 | PF_AUX_SENSOR | MET_INDICATION_ACCURACY | Indication accuracy |  |  | +/- 2% of middle half, +/- 3% first/last quarter | % |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: +/- 2% of middle half of scale and +/- 3%
PROD_PDF_QUALITROL_141 | Qualitrol 141 | PF_AUX_SENSOR | MET_DIAL_RANGE | Standard dial ranges | -10 | 10 | -10 to +10 PSI | PSI |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Standard dial ranges (optional) -10 to +10 PSI
PROD_PDF_QUALITROL_141 | Qualitrol 141 | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | Center back vertical mounting | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting Center back vertical mounting
PROD_PDF_QUALITROL_146 | Qualitrol 146 | PF_AUX_SENSOR | MET_NUMBER_OF_SWITCHES | Number of switches available |  |  | 1 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Number of switches available 1
PROD_PDF_QUALITROL_146 | Qualitrol 146 | PF_AUX_SENSOR | MET_SWITCH_CONTACT_RATING | Switch rating (AC) |  |  | 15 A @ 115, 250 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 15 A @ 115, 250 VAC
PROD_PDF_QUALITROL_148 | Qualitrol 148 | PF_AUX_SENSOR | MET_NUMBER_OF_SWITCHES | Number of switches available |  |  | 1 or 2 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Number of switches available 1 or 2
PROD_PDF_QUALITROL_148 | Qualitrol 148 | PF_AUX_SENSOR | MET_SWITCH_CONTACT_RATING | Switch rating (AC) |  |  | 15 A @ 125, 250, 480 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 15 A @ 125, 250, 480 VAC
PROD_PDF_QUALITROL_148 | Qualitrol 148 | PF_AUX_SENSOR | MET_INDICATION_ACCURACY | Indication accuracy |  |  | +/- 2% of middle half, +/- 3% first/last quarter | % |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: +/- 2% of middle half of scale and +/- 3%
PROD_PDF_QUALITROL_AKM_35600 | Qualitrol AKM 35600 | PF_AUX_SENSOR | MET_NUMBER_OF_SWITCHES | Number of switches available |  |  | 2 or 3 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Number of switches available 2 or 3
PROD_PDF_QUALITROL_AKM_35600 | Qualitrol AKM 35600 | PF_AUX_SENSOR | MET_SWITCH_CONTACT_RATING | Switch rating |  |  | 5 A @ 125 VAC; 3 A @ 250 VAC resistive | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 5 A @ 125 VAC resistive 3 A @ 250 VAC resistive
PROD_PDF_QUALITROL_AKM_35600 | Qualitrol AKM 35600 | PF_AUX_SENSOR | MET_RESPONSE_TIME | Reaction time |  | 15 | less than 15 milliseconds | ms |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/141_PressureVacuum_Switch_aefd2f72.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: react in less than 15 milliseconds when pressure changes
PROD_PDF_QUALITROL_150_151_DIRECT_MOUNT_THERMOMETERS | QUALITROL 150/151 Direct Mount Thermometers | PF_TR_TEMP | MET_INDICATION_ACCURACY | Accuracy |  |  | ±2% of dial range | % |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/150151_Indication_Only_Temperature_Indicator_99461e24.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Accuracy ± 2% of dial range
PROD_PDF_QUALITROL_150_151_DIRECT_MOUNT_THERMOMETERS | QUALITROL 150/151 Direct Mount Thermometers | PF_TR_TEMP | MET_MOUNTING_TYPE | Mounting |  |  | Side mount | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/150151_Indication_Only_Temperature_Indicator_99461e24.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting Side mount
PROD_PDF_QUALITROL_150_151_DIRECT_MOUNT_THERMOMETERS | QUALITROL 150/151 Direct Mount Thermometers | PF_TR_TEMP | MET_PROCESS_CONNECTION | Tank connection |  |  | 3/8 NPT (150) or 7/8-14 UNF-2A (151) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/150151_Indication_Only_Temperature_Indicator_99461e24.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 3/8 NPT fixed thread (150) or 7/8-14 UNF-2A (151)
PROD_PDF_QUALITROL_150_151_DIRECT_MOUNT_THERMOMETERS | QUALITROL 150/151 Direct Mount Thermometers | PF_TR_TEMP | MET_DIAL_DIAMETER | Dial diameter |  |  | 3.5" (89.7 mm) | mm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/150151_Indication_Only_Temperature_Indicator_99461e24.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dial diameter 3.5" (89.7 mm)
PROD_PDF_QUALITROL_165_167 | QUALITROL 165/167 | PF_TR_TEMP | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 1500 VAC for one minute | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dielectric strength 1500 VAC for one minute
PROD_PDF_QUALITROL_165_167 | QUALITROL 165/167 | PF_TR_TEMP | MET_PROCESS_CONNECTION | Tank connection |  |  | 165: 3/8 NPT; 167: 7/8-14 UNF-2A | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Tank connection (165 series) 3/8” NPT (standard)
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 2000 VAC for one minute | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dielectric strength 2000 VAC for one minute
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_PROCESS_CONNECTION | Tank connection |  |  | 7/8-14 UNF-2A, G 3/4”, 22 mm o-ring seal | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/165167_Direct_Temperature_Indicator_cb96e6da.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Tank connection 7/8-14 UNF -2A, G 3/4”, 22 mm o-ring seal
PROD_PDF_QUALITROL_201_SERIES | Qualitrol 201 Series | PF_AUX_SENSOR | MET_PROCESS_CONNECTION | Mounting |  |  | 1/4-18 NPT (standard) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/201_Pressure_Relief_Valves_d1b1429e.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting ¼-18 NPT (standard)
PROD_PDF_QUALITROL_201_SERIES | Qualitrol 201 Series | PF_AUX_SENSOR | MET_FLOW_RATE | Flow rate |  |  | 35 SCFM @ 15 PSIG minimum with 10 PSI operating pressure | SCFM |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/201_Pressure_Relief_Valves_d1b1429e.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Flow rate 35 SCFM @ 15 PSIG minimum with 10 PSI
PROD_PDF_QUALITROL_201_SERIES | Qualitrol 201 Series | PF_AUX_SENSOR | MET_OPERATING_PRESSURE | Operating pressure | 3.5 | 35 | 3.5, 4, 4.5, 5, 6, 8, 10, 12, 15, 20, 35 PSIG | PSIG |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/201_Pressure_Relief_Valves_d1b1429e.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Operating pressure 3.5, 4, 4.5, 5, 6, 8, 10, 12, 15, 20, 35 PSIG
PROD_PDF_QUALITROL_202_SERIES | Qualitrol 202 Series | PF_AUX_SENSOR | MET_PROCESS_CONNECTION | Mounting |  |  | 1/4-18 NPT (standard) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/201_Pressure_Relief_Valves_d1b1429e.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting ¼-18 NPT (standard)
PROD_PDF_QUALITROL_202_SERIES | Qualitrol 202 Series | PF_AUX_SENSOR | MET_FLOW_RATE | Flow rate |  |  | 50 SCFM @ 15 PSIG minimum with 10 PSI operating pressure | SCFM |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/201_Pressure_Relief_Valves_d1b1429e.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Flow rate 50 SCFM @ 15 PSIG minimum with 10 PSI
PROD_PDF_QUALITROL_202_SERIES | Qualitrol 202 Series | PF_AUX_SENSOR | MET_OPERATING_PRESSURE | Operating pressure | 3.5 | 10 | 3.5, 5, 6, 7, 8, 9, 10 PSIG | PSIG |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/201_Pressure_Relief_Valves_d1b1429e.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Operating pressure 3.5, 5, 6, 7, 8, 9, 10 PSIG
PROD_PDF_QUALITROL_205_SERIES | Qualitrol 205 Series | PF_AUX_SENSOR | MET_PROCESS_CONNECTION | Mounting |  |  | ISO 228/1-G1A, 1 1/4" - 11 1/2" NPT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/201_Pressure_Relief_Valves_d1b1429e.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting ISO 228/1-G1A, 1 1/4" - 11 1/2" NPT
PROD_PDF_QUALITROL_205_SERIES | Qualitrol 205 Series | PF_AUX_SENSOR | MET_FLOW_RATE | Flow rate |  |  | 200 SCFM @ 15 PSIG minimum with 10 PSI operating pressure | SCFM |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/201_Pressure_Relief_Valves_d1b1429e.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Flow rate 200 SCFM @ 15 PSIG minimum with 10 PSI
PROD_PDF_QUALITROL_205_SERIES | Qualitrol 205 Series | PF_AUX_SENSOR | MET_OPERATING_PRESSURE | Operating pressure | 2.9 | 11.6 | 2.9 - 11.6 PSIG (20-80 kPa) adjustable as option | PSIG |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/201_Pressure_Relief_Valves_d1b1429e.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Operating pressure 2.9 - 11.6 PSIG (20-80 kPa) adjustable
PROD_PDF_QUALITROL_206 | Qualitrol 206 | PF_AUX_SENSOR | MET_DIELECTRIC_STRENGTH | Dielectric isolation |  |  | 2500 VDC, 50/60Hz for 1 minute | VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/206_Medium_Pressure_Relief_Device_(MPRD)_8039338a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dielectric isolation 2500 VDC, 50/60Hz for 1 minute
PROD_PDF_QUALITROL_070_351_PRESSURE_VACUUM_BLEEDERS | QUALITROL 070/351 Pressure-Vacuum Bleeders | PF_AUX_SENSOR | MET_REPEATABILITY | Repeatability |  |  | ±0.5 PSI | PSI |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/351_PressureVacuum_Gauge_and_Bleeders_724e62e8.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Repeatability ± 0.5 PSI
PROD_PDF_QUALITROL_070_351_PRESSURE_VACUUM_BLEEDERS | QUALITROL 070/351 Pressure-Vacuum Bleeders | PF_AUX_SENSOR | MET_DIAL_RANGE | Dial range (070 series) |  |  | -5 to 5 PSI, -10 to 10 PSI | PSI |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/351_PressureVacuum_Gauge_and_Bleeders_724e62e8.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dial range (070 series) -5 to 5 PSI, -10 to 10 PSI
PROD_PDF_QUALITROL_070_351_PRESSURE_VACUUM_BLEEDERS | QUALITROL 070/351 Pressure-Vacuum Bleeders | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting (351 series) |  |  | Top, bottom or side mount | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/351_PressureVacuum_Gauge_and_Bleeders_724e62e8.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting (351 series) Top, bottom or side mount
PROD_PDF_QUALITROL_070_351_PRESSURE_VACUUM_BLEEDERS | QUALITROL 070/351 Pressure-Vacuum Bleeders | PF_AUX_SENSOR | MET_PROCESS_CONNECTION | Tank connection |  |  | 1/4-18 NPT, 1/8-27 NPT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/351_PressureVacuum_Gauge_and_Bleeders_724e62e8.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Tank connection 1/4-18 NPT, 1/8-27 NPT
PROD_PDF_QUALITROL_070_351_PRESSURE_VACUUM_BLEEDERS | QUALITROL 070/351 Pressure-Vacuum Bleeders | PF_AUX_SENSOR | MET_DIAL_DIAMETER | Dial diameter (070 series) |  |  | 3.5" (89 mm) | mm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/351_PressureVacuum_Gauge_and_Bleeders_724e62e8.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dial diameter (070 series) 3.5” (89 mm)
PROD_PDF_QUALITROL_T_GUARD_408 | Qualitrol T/Guard 408 | PF_TR_TEMP | MET_POWER_CONSUMPTION | Power consumption |  |  | 18 Watts | W |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/408408XT_Fiber_Optic_Winding_Temperature_Monitor_3eed4b3a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 18 Watts
PROD_PDF_QUALITROL_900_RPRR | QUALITROL 900 RPRR | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | Vertical or horizontal, flange or thread mount | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Vertical or horizontal (universal) in gas or oil space
PROD_PDF_QUALITROL_910_RPRR | QUALITROL 910 RPRR | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | Vertical or horizontal, flange or thread mount | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/900910_Rapid_Pressure_Rise_Relay_f9b730d7.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Vertical or horizontal (universal) in gas or oil space
PROD_PDF_QUALITROL_909_300_01 | Qualitrol 909-300-01 | PF_AUX_SENSOR | MET_DIELECTRIC_STRENGTH | Dielectric Strength |  |  | 2500 VAC for one minute, TB1 1-12 to 13 | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/909_Seal-In_Relay_a0e59e43.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dielectric Strength 2500 VAC for one minute
PROD_PDF_QUALITROL_930 | Qualitrol 930 | PF_AUX_SENSOR | MET_SWITCH_CONTACT_RATING | Switch rating |  |  | 120/240 VAC: 10A, 1/3 HP | A |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/930_Electronic_Pressure_Monitor_f58007ab.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 120 VAC or 240 VAC: 10A, 1/3 HP
PROD_PDF_QUALITROL_930 | Qualitrol 930 | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | 1/4”-18 NPT pressure input port; mounting studs | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/930_Electronic_Pressure_Monitor_f58007ab.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Pressure sensor: 1/4” - 18 NPT pressure input port
PROD_PDF_QUALITROL_930 | Qualitrol 930 | PF_AUX_SENSOR | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 1500 VAC common mode for 60 seconds | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/930_Electronic_Pressure_Monitor_f58007ab.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 1500 VAC common mode on TB3-1,2,4-9 to TB3-3 for 60 seconds
PROD_PDF_QUALITROL_AKM345_GEN3_OTIWTI | Qualitrol AKM345 Gen3 OTIWTI | PF_TR_TEMP | MET_INDICATION_ACCURACY | Indication Accuracy |  |  | ±2% of full dial range | % |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM345_Gen3_Oil_and_Winding_Temperature_Indicator_09e05650.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Indication Accuracy ±2% of full dial range
PROD_PDF_QUALITROL_AKM345_GEN3_OTIWTI | Qualitrol AKM345 Gen3 OTIWTI | PF_TR_TEMP | MET_MOUNTING_TYPE | Mounting Style |  |  | Stainless Steel anti-vibration, Elastomeric seismic, or Universal mount | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM345_Gen3_Oil_and_Winding_Temperature_Indicator_09e05650.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Stainless Steel anti-vibration mount (standard), Elastomeric seismic mount, or Universal mount
PROD_PDF_QUALITROL_AKM345_GEN3_OTIWTI | Qualitrol AKM345 Gen3 OTIWTI | PF_TR_TEMP | MET_NUMBER_OF_SWITCHES | Number of Switches | 2 | 6 | 2, 4, or 6 independently adjustable switches | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM345_Gen3_Oil_and_Winding_Temperature_Indicator_09e05650.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 2, 4, or 6 independently adjustable switches
PROD_PDF_QUALITROL_AKM345_GEN3_OTIWTI | Qualitrol AKM345 Gen3 OTIWTI | PF_TR_TEMP | MET_SWITCH_CONTACT_RATING | Switch Rating |  |  | up to 15 Amps VAC, up to 10 Amp DC | A |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM345_Gen3_Oil_and_Winding_Temperature_Indicator_09e05650.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: switch rated for up to 15 Amps VAC and up to 10 Amp DC switches
PROD_PDF_QUALITROL_AKM345_GEN3_OTIWTI | Qualitrol AKM345 Gen3 OTIWTI | PF_TR_TEMP | MET_INDICATION_ACCURACY | Switching Accuracy |  |  | ±3% of full dial range | % |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM345_Gen3_Oil_and_Winding_Temperature_Indicator_09e05650.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Switching Accuracy ±3% of full dial range
PROD_PDF_QUALITROL_AKM345_GEN3_OTIWTI | Qualitrol AKM345 Gen3 OTIWTI | PF_TR_TEMP | MET_STORAGE_TEMP | Storage Temperature | -50 | 80 | -50° to 80°C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM345_Gen3_Oil_and_Winding_Temperature_Indicator_09e05650.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Storage Temperature -50° to 80°C
PROD_PDF_QUALITROL_AKM_35600 | QUALITROL AKM 35600 | PF_AUX_SENSOR | MET_SWITCH_RATING_DC | Switch rating (DC) |  |  | 0.8 A @ 110 VDC resistive; 0.6 A @ 125 VDC; 0.4 A @ 220 VDC | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_35600_Pressure_Control_Switches_86b46020.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 0.8 A @ 110 VDC resistive 0.6 A @ 125 VDC resistive
PROD_PDF_QUALITROL_AKM_35600 | QUALITROL AKM 35600 | PF_AUX_SENSOR | MET_PROCESS_CONNECTION | Tank connection |  |  | 1/4-18 NPT, 5/16 compression, G3/8, M26 x 1.5 mm, flange 110 mm | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_35600_Pressure_Control_Switches_86b46020.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: 1/4-18 NPT, 5/16 compression fitting, G3/8, M26 x 1.5 mm
PROD_PDF_QUALITROL_AKM_35600 | QUALITROL AKM 35600 | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | Center back vertical, horizontal possible for some models | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_35600_Pressure_Control_Switches_86b46020.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Center back vertical mounting but also horizontal possible
PROD_PDF_AKM_44611_48471 | AKM 44611/48471 | PF_TR_TEMP | MET_INDICATION_ACCURACY | Accuracy |  |  | ±2ºC between 50-120ºC | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_4461148471_Bi-Metal_Thermometer_71abb218.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Accuracy 2ºC between 50-120ºC
PROD_PDF_AKM_44611_48471 | AKM 44611/48471 | PF_TR_TEMP | MET_MOUNTING_TYPE | Mounting |  |  | Top mounting | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_4461148471_Bi-Metal_Thermometer_71abb218.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting Top mounting
PROD_PDF_AKM_44611_48471 | AKM 44611/48471 | PF_TR_TEMP | MET_PROCESS_CONNECTION | Tank connection |  |  | G 1/2", G 3/4", G 1.0", 22 mm O-ring seal | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_4461148471_Bi-Metal_Thermometer_71abb218.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Tank connection G 1/2", G 3/4", G 1.0", 22 mm O-ring seal
PROD_PDF_AKM_44611_48471 | AKM 44611/48471 | PF_TR_TEMP | MET_PROBE_LENGTH | Probe length | 100 | 110 | 100 mm, 110 mm | mm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_4461148471_Bi-Metal_Thermometer_71abb218.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Probe length 3.94", 4.33" (100 mm, 110 mm)
PROD_PDF_AKM_44612_44622_44617_44618_44650 | AKM 44612/44622/44617/44618/44650 | PF_TR_TEMP | MET_INDICATION_ACCURACY | Switching accuracy |  |  | ±3ºC between 50°C and 120ºC | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_44612446224461744618_Thermometer_188b5fee.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switching accuracy ±3ºC between 50°C and 120ºC
PROD_PDF_AKM_44612_44622_44617_44618_44650 | AKM 44612/44622/44617/44618/44650 | PF_TR_TEMP | MET_MOUNTING_TYPE | Mounting |  |  | Top mount | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_44612446224461744618_Thermometer_188b5fee.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting Top mount
PROD_PDF_AKM_44612_44622_44617_44618_44650 | AKM 44612/44622/44617/44618/44650 | PF_TR_TEMP | MET_DIELECTRIC_STRENGTH | Dielectric isolation |  |  | 2000 VAC for one minute | V AC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_44612446224461744618_Thermometer_188b5fee.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dielectric isolation 2000 VAC for one minute
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_MOUNTING_TYPE | Mounting |  |  | Side (center back thread) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_47080_Direct_Mount_Bimetal_Thermometer_1a28ed38.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting Side (center back thread)
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_INDICATION_ACCURACY | Accuracy |  |  | +/- 2% of dial range | % |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_47080_Direct_Mount_Bimetal_Thermometer_1a28ed38.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Accuracy +/- 2% of dial range
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_NUMBER_OF_SWITCHES | Maximum number of switches |  | 2 | 2 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_47080_Direct_Mount_Bimetal_Thermometer_1a28ed38.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Maximum number of switches 2
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_SWITCH_RATING_AC | Switch rating (AC) |  |  | 5A @ 250 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_47080_Direct_Mount_Bimetal_Thermometer_1a28ed38.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 5A @ 250 VAC
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_SWITCH_RATING_DC | Switch rating (DC) |  |  | 0.3A @ 110 VDC - inductive (L/R=10 ms) | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_47080_Direct_Mount_Bimetal_Thermometer_1a28ed38.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: 0.3A @ 110 VDC - inductive (L/R=10 ms)
PROD_PDF_AKM_47080 | AKM 47080 | PF_TR_TEMP | MET_CASE_MATERIAL | Case material |  |  | Die-cast aluminum, ASA #70 light grey finish | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_47080_Direct_Mount_Bimetal_Thermometer_1a28ed38.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Case Die-cast aluminum, ASA #70 light grey finish
PROD_PDF_QUALITROL_032_042_045_LARGE_OIL_LEVEL_INDICATOR | QUALITROL 032/042/045 Large Oil Level Indicator | PF_AUX_SENSOR | MET_NUMBER_OF_SWITCHES | Number of switches |  | 3 | Up to 3 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Number of switches Up to 3
PROD_PDF_QUALITROL_032_042_045_LARGE_OIL_LEVEL_INDICATOR | QUALITROL 032/042/045 Large Oil Level Indicator | PF_AUX_SENSOR | MET_SWITCH_RATING_AC | Switch rating (AC) |  |  | 10A @ 125, 250, 480 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 10A @ 125, 250, 480 VAC
PROD_PDF_QUALITROL_032_042_045_LARGE_OIL_LEVEL_INDICATOR | QUALITROL 032/042/045 Large Oil Level Indicator | PF_AUX_SENSOR | MET_SWITCH_RATING_DC | Switch rating (DC) |  |  | 1/2A @ 125 VDC, 1/4A @ 250 VDC resistive | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 1/2A @ 125 VDC, resistive 1/4A @ 250 VDC, resistive
PROD_PDF_QUALITROL_032_042_045_LARGE_OIL_LEVEL_INDICATOR | QUALITROL 032/042/045 Large Oil Level Indicator | PF_AUX_SENSOR | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 1,500 VAC for 60 seconds | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Dielectric strength 1,500 VAC for 60 seconds
PROD_PDF_QUALITROL_032_042_045_LARGE_OIL_LEVEL_INDICATOR | QUALITROL 032/042/045 Large Oil Level Indicator | PF_AUX_SENSOR | MET_MAX_LOAD | Max load |  |  | 600Ω | ohm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Max load 600Ω
PROD_PDF_QUALITROL_032_042_045_LARGE_OIL_LEVEL_INDICATOR | QUALITROL 032/042/045 Large Oil Level Indicator | PF_AUX_SENSOR | MET_DIAL_DIAMETER | Dial diameter |  |  | 5.5" (140mm) | in/mm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Dial diameter 5.5" (140mm)
PROD_PDF_QUALITROL_032_042_045_LARGE_OIL_LEVEL_INDICATOR | QUALITROL 032/042/045 Large Oil Level Indicator | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | Flange mount, various sizes available | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Mounting Flange mount, various sizes available
PROD_PDF_QUALITROL_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATOR | QUALITROL AKM 44712 / 34725 Large Oil Level Indicator | PF_AUX_SENSOR | MET_NUMBER_OF_SWITCHES | Number of switches |  | 4 | 4 | count |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Number of switches 4
PROD_PDF_QUALITROL_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATOR | QUALITROL AKM 44712 / 34725 Large Oil Level Indicator | PF_AUX_SENSOR | MET_SWITCH_RATING_AC | Switch rating (AC) |  |  | 5A @ 250 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 5A @ 250 VAC
PROD_PDF_QUALITROL_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATOR | QUALITROL AKM 44712 / 34725 Large Oil Level Indicator | PF_AUX_SENSOR | MET_SWITCH_RATING_DC | Switch rating (DC) |  |  | 0.30A @ 125 VDC, resistive | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (DC) 0.30A @ 125 VDC, resistive
PROD_PDF_QUALITROL_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATOR | QUALITROL AKM 44712 / 34725 Large Oil Level Indicator | PF_AUX_SENSOR | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 2,000 VAC for 60 seconds | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dielectric strength 2,000 VAC for 60 seconds
PROD_PDF_QUALITROL_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATOR | QUALITROL AKM 44712 / 34725 Large Oil Level Indicator | PF_AUX_SENSOR | MET_MAX_LOAD | Max load |  |  | 600Ω | ohm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Max load 600Ω
PROD_PDF_QUALITROL_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATOR | QUALITROL AKM 44712 / 34725 Large Oil Level Indicator | PF_AUX_SENSOR | MET_DIAL_DIAMETER | Dial diameter |  |  | 5.9" (150mm) or 9.8" (250mm) | in/mm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dial diameter 5.9" (150 mm) or 9.8" (250 mm)
PROD_PDF_QUALITROL_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATOR | QUALITROL AKM 44712 / 34725 Large Oil Level Indicator | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | M50 thread mount | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_Oil_Level_Indicator_65d66203.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Mounting M50 thread mount
PROD_PDF_AKM_OLR | AKM OLR | PF_AUX_SENSOR | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 2000 VAC for one minute | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_OLR_Remote_Mechanical_Oil_Level_Indicator_ad31eee0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dielectric strength 2000 VAC for one minute
PROD_PDF_QUALITROL_KIT_930 | QUALITROL KIT-930 | PF_AUX_SENSOR | MET_ANALOG_OUTPUT | Analog output signal | 4 | 20 | 4 - 20 mA @ maximum 500 Ohms for RH | mA |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Field_Kit_for_930_Pressure_Monitor_5e0de6e3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 4 - 20 mA @ maximum 500 Ohms for RH
PROD_PDF_QUALITROL_KIT_930 | QUALITROL KIT-930 | PF_AUX_SENSOR | MET_DIELECTRIC_STRENGTH | Dielectric isolation |  |  | 1500 VAC for 60 seconds to ground | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Field_Kit_for_930_Pressure_Monitor_5e0de6e3.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 1500 VAC for 60 seconds to ground
PROD_PDF_QUALITROL_505_ITM | Qualitrol 505 ITM | PF_TR_TEMP | MET_INDICATION_ACCURACY | Input accuracy |  |  | ± 0.5 % full-scale input range | % |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_505_88332a90.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: Accuracy ± 0.5 % full-scale input range
PROD_PDF_QUALITROL_509_ITM | QUALITROL 509 ITM | PF_TR_TEMP | MET_INDICATION_ACCURACY | Input accuracy |  |  | ±0.5% full-scale input range | % |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/ITM_509_369c448e.pdf (page 7) | Datasheet-sourced (Step 0b). Evidence: ± 0.5% full-scale input range
PROD_PDF_QUALITROL_LPRD | QUALITROL LPRD | PF_AUX_SENSOR | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 2500 VAC, 50/60 Hz for one minute | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/LPRD_Large_Pressure_Relief_Devices_72428d97.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: 2500 VAC, 50/60 Hz. for one minute
PROD_PDF_QUALITROL_LPRD | QUALITROL LPRD | PF_AUX_SENSOR | MET_MOUNTING_TYPE | Mounting |  |  | Top mounted horizontal (recommended) or side mounted vertical | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/LPRD_Large_Pressure_Relief_Devices_72428d97.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: top mounted horizontally (recommended) or side mounted vertically
PROD_PDF_QUALITROL_LPRD | QUALITROL LPRD | PF_AUX_SENSOR | MET_PROCESS_CONNECTION | Electrical connection style |  |  | QUALITROL circular 3 pin, ANSI 3 pin, MS3102E16-10P, flying leads or terminal box | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/LPRD_Large_Pressure_Relief_Devices_72428d97.pdf (page 5) | Datasheet-sourced (Step 0b). Evidence: QUALITROL style circular 3 pin, ANSI style circular 3 pin
PROD_PDF_NEOPTIX_T1_PROBE | Neoptix T1 Probe | PF_TR_TEMP | MET_REPEATABILITY | Repeatability |  |  | ±0.1 ºC | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Neoptix_T1_Fiber_Optic_Temperature_Probe_cf61e6a9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Repeatability: ±0.1 ºC
PROD_PDF_NEOPTIX_T1_PROBE | Neoptix T1 Probe | PF_TR_TEMP | MET_INDICATION_ACCURACY | Accuracy (without user reference) |  |  | ±1 ºC | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Neoptix_T1_Fiber_Optic_Temperature_Probe_cf61e6a9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Accuracy (without user reference): ±1 ºC
PROD_PDF_NEOPTIX_T1_PROBE | Neoptix T1 Probe | PF_TR_TEMP | MET_INDICATION_ACCURACY | Accuracy (with user reference) |  |  | ±0.2 ºC at ±10 ºC of calibration point | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Neoptix_T1_Fiber_Optic_Temperature_Probe_cf61e6a9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Accuracy (with user reference): ±0.2 ºC at ±10 º C
PROD_PDF_NEOPTIX_T1_PROBE | Neoptix T1 Probe | PF_TR_TEMP | MET_RESPONSE_TIME | Response time (63% of final value) |  |  | 250 msec for standard probe | msec |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Neoptix_T1_Fiber_Optic_Temperature_Probe_cf61e6a9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Response time (63% of final value): 250 msec
PROD_PDF_NEOPTIX_T1_PROBE | Neoptix T1 Probe | PF_TR_TEMP | MET_PROBE_LENGTH | Probe length | 2 | 300 | 2 meters standard, up to 300 meters | m |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Neoptix_T1_Fiber_Optic_Temperature_Probe_cf61e6a9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Probe length: 2 meters standard, up to 300 meters
PROD_PDF_QUALITROL_NEOPTIX_T2_PROBE_T2S | Qualitrol Neoptix T2 Probe (T2S) | PF_TR_TEMP | MET_INDICATION_ACCURACY | System accuracy |  |  | ±1 °C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Neoptix_T2_Transformer_Temperature_Probe_7024aafc.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Accuracy ±1 oC (system accuracy)
PROD_PDF_QUALITROL_NEOPTIX_T2_PROBE_T2S | Qualitrol Neoptix T2 Probe (T2S) | PF_TR_TEMP | MET_RESPONSE_TIME | Response time |  |  | 250 milliseconds | ms |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Neoptix_T2_Transformer_Temperature_Probe_7024aafc.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Response time 250 milliseconds
PROD_PDF_QUALITROL_NEOPTIX_T2_PROBE_T2S | Qualitrol Neoptix T2 Probe (T2S) | PF_TR_TEMP | MET_PROBE_LENGTH | Probe lengths | 1 | 15 | 1 to 15 meters, up to 500 m special request | m |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Neoptix_T2_Transformer_Temperature_Probe_7024aafc.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Probe lengths 1 to 15 meters, in increments of 1 meter
PROD_PDF_QUALITROL_NEOPTIX_T2_PROBE_T2S | Qualitrol Neoptix T2 Probe (T2S) | PF_TR_TEMP | MET_DIELECTRIC_STRENGTH | Optical fiber dielectric strength |  |  | >15,000 V/mm | V/mm |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Neoptix_T2_Transformer_Temperature_Probe_7024aafc.pdf (page 1) | Datasheet-sourced (Step 0b). Evidence: Dielectric strength: >15,000 V/mm
PROD_PDF_NOMAD_DIRECT | NOMAD-Direct | PF_TR_TEMP | MET_RESPONSE_TIME | Response Time |  |  | 0.5 seconds | seconds |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/NOMAD-Direct_Fiber-Optic_Temperature_Monitor_d7b954be.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Response Time 0.5 seconds
PROD_PDF_NOMAD_DIRECT | NOMAD-Direct | PF_TR_TEMP | MET_STORAGE_TEMP | Storage Temperature | -20 | 50 | -20 °C to 50 °C | °C |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/NOMAD-Direct_Fiber-Optic_Temperature_Monitor_d7b954be.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Storage Temperature -20 °C to 50 °C
PROD_PDF_NOMAD_DIRECT | NOMAD-Direct | PF_TR_TEMP | MET_WEIGHT | Weight |  |  | 1 kg | kg |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/NOMAD-Direct_Fiber-Optic_Temperature_Monitor_d7b954be.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Weight 1 kg
PROD_PDF_QUALITROL_QHS393 | Qualitrol QHS393 | PF_AUX_SENSOR | MET_RESPONSE_TIME | Response time t90 |  |  | < 60 sec | sec |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Oil_and_Moisture_Temperature_Sensor_acc1b1e0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Response time t :90 < 60 sec
PROD_PDF_QUALITROL_QHS393 | Qualitrol QHS393 | PF_AUX_SENSOR | MET_POWER_CONSUMPTION | Power consumption at 24 V DC |  |  | Max. 80 mA | mA |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Oil_and_Moisture_Temperature_Sensor_acc1b1e0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Power consumption at 24 V DC: Max. 80 mA
PROD_PDF_QUALITROL_QHS393 | Qualitrol QHS393 | PF_AUX_SENSOR | MET_PROCESS_CONNECTION | Connection |  |  | ½” NPT | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/Oil_and_Moisture_Temperature_Sensor_acc1b1e0.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: ½" NPT Connection.
PROD_PDF_T_GUARD_LINK_REVB | T/Guard-Link RevB | PF_TR_TEMP | MET_POWER_CONSUMPTION | Consumption |  |  | 6 watts | W |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TGuard_Link_RevB_Fiber-Optic_Hot-Spot_Monitor_b37a6673.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Consumption 6 watts
PROD_PF_DGA_01 | Serveron TM1 | PF_DGA | MET_OPERATING_PRESSURE | Oil Inlet Pressure | 0 | 100 | 0 to 100 psi (0 to 7 bar) | psi |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM1_ad935707.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Oil Inlet Pressure 0 to 100 psi (0 to 7 bar)
PROD_PF_DGA_02 | Serveron TM3 | PF_DGA | MET_OPERATING_PRESSURE | Oil Inlet Pressure | 0 | 3 | 0 to 45 psi (0 to 3 bar) | bar |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/TM3_73e234b6.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Oil Inlet Pressure 0 to 45 psi (0 to 3 bar)
PROD_PDF_QUALITROL_XPRD | Qualitrol XPRD | PF_AUX_SENSOR | MET_FLOW_RATE | Flow rate |  |  | 12,600 SCFM at 15 PSI with 10 PSI operating pressure | SCFM |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/XPRD_Extra_Large_Pressure_Relief_Device_cf600595.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Flow rate of 12,600 SCFM—independently verified by third party
PROD_PDF_QUALITROL_XPRD | Qualitrol XPRD | PF_AUX_SENSOR | MET_DIELECTRIC_STRENGTH | Dielectric strength |  |  | 2000 VAC, 50/60 Hz for 1 minute | VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/XPRD_Extra_Large_Pressure_Relief_Device_cf600595.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Dielectric strength 2000 VAC, 50/60 Hz for 1 minute
PROD_PDF_QUALITROL_032_042_045_LARGE_OIL_LEVEL_INDICATOR | Qualitrol 032/042/045 Large Oil Level Indicator | PF_AUX_SENSOR | MET_FLOAT_MECHANISM | Float mechanism |  |  | Gear (042 and 045 series) or lever (032 series) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/045_Liquid_Level_Gauge_09f522e9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Gear (042 and 045 series) or lever (032 series)
PROD_PDF_QUALITROL_032_042_045_LARGE_OIL_LEVEL_INDICATOR | Qualitrol 032/042/045 Large Oil Level Indicator | PF_AUX_SENSOR | MET_ANALOG_OUTPUT | SCADA output signal |  |  | 4-20mA or 0-1mA (Only with 039 Remote Enclosure) | mA |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/045_Liquid_Level_Gauge_09f522e9.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: 4 - 20mA or 0 - 1mA (Only with 039 Remote Enclosure)
PROD_PDF_QUALITROL_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATOR | Qualitrol AKM 44712/34725 Large Oil Level Indicator | PF_AUX_SENSOR | MET_FLOAT_MECHANISM | Float mechanism |  |  | Gear (34725) or lever (44712) | text |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/045_Liquid_Level_Gauge_09f522e9.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Float mechanism Gear (34725) or lever (44712)
PROD_PDF_QUALITROL_AKM_44712_34725_LARGE_OIL_LEVEL_INDICATOR | Qualitrol AKM 44712/34725 Large Oil Level Indicator | PF_AUX_SENSOR | MET_ANALOG_OUTPUT | SCADA output signal |  |  | 4-20 mA | mA |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/045_Liquid_Level_Gauge_09f522e9.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Output signal 4 - 20 mA
PROD_PDF_QUALITROL_141 | QUALITROL 141 | PF_AUX_SENSOR | MET_SWITCH_RATING_DC | Switch rating (DC) |  |  | ½ A @ 125 VDC, ¼ A @ 250 VDC resistive | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/146_PressureVacuum_Switch_ddef168f.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: ½ A @ 125 VDC, resistive
PROD_PDF_QUALITROL_148 | QUALITROL 148 | PF_AUX_SENSOR | MET_DIAL_RANGE | Standard dial ranges | -10 | 10 | -10 to +10 PSI | PSI |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/146_PressureVacuum_Switch_ddef168f.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Standard dial ranges (optional) - 10 to +10 PSI
PROD_PDF_QUALITROL_141 | QUALITROL 141 | PF_AUX_SENSOR | MET_SWITCH_RATING_AC | Switch rating (AC) |  |  | 15 A @ 125, 250, 480 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/148_PressureVacuum_Switch_2a33e83a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 15 A @ 125, 250, 480 VAC
PROD_PDF_QUALITROL_146 | QUALITROL 146 | PF_AUX_SENSOR | MET_SWITCH_RATING_AC | Switch rating (AC) |  |  | 15 A @ 115, 250 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/148_PressureVacuum_Switch_2a33e83a.pdf (page 3) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 15 A @ 115, 250 VAC
PROD_PDF_QUALITROL_148 | QUALITROL 148 | PF_AUX_SENSOR | MET_SWITCH_RATING_AC | Switch rating (AC) |  |  | 15 A @ 125, 250, 480 VAC | A/VAC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/148_PressureVacuum_Switch_2a33e83a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: Switch rating (AC) 15 A @ 125, 250, 480 VAC
PROD_PDF_QUALITROL_148 | QUALITROL 148 | PF_AUX_SENSOR | MET_SWITCH_RATING_DC | Switch rating (DC) |  |  | ½ A @ 125 VDC, ¼ A @ 250 VDC resistive | A/VDC |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/148_PressureVacuum_Switch_2a33e83a.pdf (page 4) | Datasheet-sourced (Step 0b). Evidence: ½ A @ 125 VDC, resistive
PROD_PDF_AKM_35600_47500 | AKM 35600 / 47500 | PF_AUX_SENSOR | MET_REPEATABILITY | Repeatability of switch set points |  |  | +/-5% or +/- 0.4 PSI (3 kPa) | %/PSI |  |  | Preparation/Qualitrol Product/Transformer_Monitoring/AKM_47500_Pressure_Control_Switches_1068660c.pdf (page 2) | Datasheet-sourced (Step 0b). Evidence: Repeatability of +/-5% or +/- 0.4 PSI (3 kPa)

## 09_Quantity_Rules
Quantity Rules - Explainable BOQ Quantity Logic
BOQ quantities should be derived from these rules plus the drawing/equipment-derived Asset List.
Quantity Rule ID | Scenario ID | Product Family ID | Product Family | Quantity Basis | Rule Description | Need Drawing | Need Asset List | Count Field | Example | Assumption / Risk
| ';'-separated scenarios (sheet 03) this rule applies to. | Family (sheet 06) this rule sizes. | Family display name. | What quantity scales with; shown in BOQ output. | Human-readable rule; mainly for display/review. | Reference flag; not enforced by code. | Reference flag; not enforced by code. | KEY: count field mapped in constants.py to a metric/asset count for sizing. | Reference example; not used by code. | Assumption text written into the BOQ offer notes.
QR_TR_DGA_001 | TR_DGA_001 | PF_DGA | Online DGA Monitor | Transformer count | Default: 1 DGA monitor per monitored oil-filled transformer. | Recommended | Yes | transformer_count | Two oil-filled main transformers T1 and T2 => Qty 2 | Do not apply to dry-type transformers.
QR_TR_TEMP_001 | TR_TEMP_001; DRY_TR_TEMP_001 | PF_TR_TEMP | Transformer Temperature Monitor | Transformer count | Default: 1 temperature monitor per transformer or transformer control cabinet. | Optional | Yes | transformer_count | Three dry-type transformers => Qty 3 | Cooling stage/channel count may change configuration.
QR_TR_BUSH_001 | TR_BUSH_001 | PF_BUSHING | Bushing Monitor | Transformer count and bushing/channel count | Default: 1 system per transformer; channels depend on monitored bushing count. | Recommended | Yes | bushing_count | Two transformers with 6 bushings each => 2 systems / 12 channels | Needs bushing configuration.
QR_TR_PD_001 | TR_PD_001 | PF_PD_TRANSFORMER | Transformer PD Monitor | Monitoring zone / sensor count | Quantity depends on transformer design and selected PD sensor method. | Recommended | Yes | sensor_count | One transformer with 3 UHF sensors => Qty per engineering design | Requires product engineer review.
QR_TR_AUX_001 | TR_AUX_001 | PF_AUX_SENSOR | Transformer Auxiliary Sensors | Accessory point count | Quantity equals required accessories or protection points per transformer. | Optional | Yes | accessory_count | One PRD + one oil level indicator per transformer | Accessory scope may be provided by OEM.
QR_BRK_001 | BRK_HEALTH_001 | PF_BREAKER | Circuit Breaker Monitor | Breaker count | Default: 1 breaker monitor per monitored circuit breaker. | Recommended | Yes | breaker_count | Six 220kV breakers => Qty 6 | Confirm whether one monitor can cover multiple mechanisms depending on product architecture.
QR_GIS_PD_001 | GIS_PD_001 | PF_GIS_PD | GIS PD Monitor | GIS bay / compartment / monitoring zone count | Quantity based on GIS layout, bays, compartments, and sensor placement. | Strongly Required | Yes | gis_bay_count | Eight GIS bays with defined UHF sensor locations => engineering-derived Qty | Do not estimate without GIS layout.
QR_SWG_PD_001 | SWG_PD_001 | PF_SWG_PD | MV Switchgear PD Monitor | Panel / feeder / sensor count | Quantity depends on switchgear lineup and panel/feeder coverage. | Required | Yes | panel_count | Twelve MV panels => Qty depends on panel-level or group-level design | Scope must define feeder vs lineup coverage.
QR_GEN_PD_001 | GEN_PD_001 | PF_GEN_PD | Generator PD Monitor | Generator unit count | Default: 1 monitoring system per generator; sensor/coupler count per design. | Recommended | Yes | generator_count | Four generator units => Qty 4 systems plus couplers | Coupler count requires generator design review.
QR_GEN_EWV_001 | GEN_EWV_001 | PF_GEN_EWV | Generator End-Winding Vibration Monitor | Generator unit and sensor location count | Quantity based on generator units and end-winding sensor locations. | Required | Yes | sensor_count | One generator with 12 vibration sensors => Qty per system/channel capacity | Engineering review required.
QR_GEN_AIRGAP_001 | GEN_AIRGAP_001 | PF_GEN_AIRGAP | Hydro Generator Air Gap / Rotor Monitor | Hydro unit count and sensor layout | Quantity based on each hydro unit and air gap/flux sensor layout. | Required | Yes | generator_count | Two hydro units => two systems plus sensor sets | Design-specific.
QR_MOTOR_001 | MTR_PD_001; MTR_TEMP_001 | PF_MOTOR | Motor Monitor | Critical motor count and channel count | Default: 1 monitoring system per monitored critical motor; channels depend on RTD/sensor count. | Optional | Yes | motor_count | Eight compressor motors => Qty 8 systems or channel groups | Can be grouped depending on product architecture.
QR_PQ_001 | PQ_CLASSA_001 | PF_PQ | Power Quality Recorder | PCC / bus / feeder count | Default: 1 PQ recorder per monitored PCC, bus, or feeder. | Strongly Recommended | Yes | pcc_count | One grid connection point => Qty 1 | Channel count and Class A requirement must be checked.
QR_DFR_001 | DFR_DDR_001 | PF_DFR | Digital Fault / Disturbance Recorder | Channel group / station / bus count | Quantity based on voltage/current channel count and monitored points. | Required | Yes | channel_count | One station with 16 current and 8 voltage channels => product/channel configuration | Channel count drives configuration.
QR_PMU_001 | PMU_001 | PF_PMU | Phasor Measurement Unit | Measurement point count | Default: 1 PMU per monitored bus/PCC/measurement point unless integrated with recorder. | Recommended | Yes | measurement_point_count | Two monitored buses => Qty 2 | Confirm standalone vs integrated PMU.
QR_SOFT_001 | SUB_SOFT_001 | PF_SOFTWARE | Monitoring Software / Asset Platform | Site / asset / tag / user count | Quantity/license depends on software licensing model. | Optional | Yes | asset_count_or_tag_count | Five substations with 200 assets => license TBD | Commercial team must confirm license model.
QR_GATEWAY_001 | COMM_SCADA_001 | PF_GATEWAY | Communication Gateway / Integration Module | Site / protocol boundary / network segment count | Quantity based on integration architecture and protocol conversion boundaries. | Optional | Yes | site_count_or_gateway_count | One Modbus-to-IEC61850 gateway per substation | May be accessory rather than BOQ line.
QR_DAU_BAY_001 | FMS_001;DFR_DDR_001;PMU_001;WAMS_001;PQ_CLASSA_001 | PF_DAU_REC | Multi-function DAU / Recorder (IDM+ / Informa) | Monitored bay count (per voltage level & function) | One DAU per monitored bay, per function (FMS/PQM/PMU), sized by voltage level (27A/64D on 400kV OHL bays; 9A/32D on 132/11kV). | Required | Yes | measurement_point_count | 14 IDM+ for 14 monitored 400kV bays; 9 Informa for 9 PQ bays. | Count *monitored* bays (not raw feeder labels); confirm per-voltage split.
QR_PANEL_001 | FMS_001;PMU_001;WAMS_001;PQ_CLASSA_001 | PF_MON_PANEL | Monitoring Panel / Cabinet | Panel count from DAU grouping | One field panel per ~2 DAUs plus one LEV/PDC system cabinet per station. | Optional | No | panel_count | 6 FMS/WAMS panels + 5 FMS/PQM panels + LEV/PDC cabinets. | Panel grouping per Transco spec; confirm with engineering.
QR_PER_PANEL_001 | COMM_SCADA_001 | PF_NET_SEC | Network & Security Equipment | Per panel | Switches/firewalls per panel and per LEV/PDC cabinet as per comms architecture. | Optional | No | panel_count | 2× L2 + 2× L3 switch per LEV; firewalls per cabinet. | Depends on network architecture; confirm.
QR_PER_SYSTEM_001 | COMM_SCADA_001;PMU_001;WAMS_001 | PF_SW_LIC | Monitoring Software & Licences | 1 per substation/system | System-level software / licences / timing quoted once per substation (licences may scale by PMU/WAMS channel). | No | No | site_count | 1× iQ+ per station; EPG PMU licences per PMU channel. | Confirm licence/user tiers and redundancy.
QR_PER_DAU_001 | FMS_001;PMU_001;PQ_CLASSA_001 | PF_PANEL_ACC | Panel Accessories | Per DAU | Accessories (test switches etc.) counted per DAU/bay. | No | No | measurement_point_count | One set of test switches per DAU. | Confirm accessory list per DAU.
QR_SERVICES_001 | COMM_SCADA_001 | PF_SERVICES | Engineering & Commissioning Services | Per project (day-rate estimate) | Service days scale with panel/bay count; quoted as day-rate + mobilisation. | No | No | site_count | FAT 5 days; commissioning 25 days for a large GS. | Day estimates need engineer confirmation.

## 10_Compatibility_Rules
Compatibility Rules - Guardrails for Product Matching
Use these rules before AI-generated explanations. Product matching should be rules-first and AI-explained.
Rule ID | Rule Type | Scenario ID | Asset Type | Condition / Trigger | Recommended Action | Severity | Notes
| Exclusion/Must-have; controls how the rule is evaluated. | Scenario (sheet 03) guarded; 'All' applies to every scenario. | Reference; asset the rule concerns. | Condition text; heuristically matched in Step 2 to decide firing. | Action/message emitted when the rule triggers. | High/Medium/Low; High+triggered sends the line to review. | Human note; not used by the pipeline.
CR_001 | Exclusion | TR_DGA_001 | Oil vs dry-type transformer | Asset is a dry-type (non-oil) transformer | Do not recommend oil DGA monitors; a dry-type transformer has no insulating oil to sample. | High | Prevents false DGA recommendation.
CR_002 | Must-have | PQ_CLASSA_001 | PCC / bus / feeder | Customer requires Class A power quality (IEC 61000-4-30) | Only offer recorders certified IEC 61000-4-30 Class A; do not downgrade to Class S/B. | High | Class A is a hard compliance gate.
CR_003 | Must-have | COMM_SCADA_001 | Monitoring system / integration | Customer specifies a SCADA protocol (IEC 61850 / DNP3 / Modbus) | Confirm the offered product supports the required protocol; flag any gap. | High | Protocol mismatch blocks integration.
CR_020 | Exclusion | DRY_TR_TEMP_001 | Dry-type transformer | Asset is a dry-type transformer | Do not recommend oil-immersed temperature probes; use RTD / fibre-optic dry-type temperature monitoring. | High | Oil-based sensors do not apply to dry-type.
CR_021 | Exclusion | GEN_PD_001 | Generator vs motor | Asset is a motor, not a generator | Do not use the generator stator PD family; route to the motor monitoring family. | High | Avoid generator/motor cross-asset mismatch.
CR_022 | Exclusion | GIS_PD_001 | GIS vs AIS | Switchgear is air-insulated (AIS), not gas-insulated (GIS) | Do not recommend the GIS UHF PD product; use the MV switchgear PD family instead. | High | GIS UHF couplers do not fit AIS.
CR_023 | Exclusion | MTR_PD_001 | Motor voltage class | Motor is low-voltage (< 3 kV) | Do not recommend HV/MV stator PD monitoring; PD monitoring targets MV/HV machines. | Medium | PD monitoring uncommon on LV motors.
CR_024 | Exclusion | SWG_PD_001 | Switchgear type | Switchgear is gas-insulated (GIS), not conventional MV switchgear | Use the GIS PD family; the MV switchgear PD product may not suit true GIS. | Medium | Route GIS to the GIS PD family.
CR_025 | Must-have | PMU_001 | Grid measurement point | Synchrophasor / PMU measurement is required | Offer only PMUs compliant with IEEE C37.118 (and IEC 61850-90-5 protocol where required). | High | Synchrophasor standard is mandatory.
CR_026 | Must-have | DFR_DDR_001 | Substation / feeder | Digital fault / disturbance recording is required | Offer recorders supporting COMTRADE and IEC 61850 protocol; confirm analogue/digital channel capacity. | High | Records must be standard-format.
CR_027 | Must-have | GIS_PD_001 | GIS bay | GIS partial discharge monitoring is required | Offer UHF-sensor-based PD monitoring suitable for GIS; confirm UHF coupler mounting feasibility. | High | GIS PD is UHF-based.
CR_028 | Must-have | SWG_PD_001 | MV switchgear | MV switchgear partial discharge monitoring is required | Confirm the sensor method (UHF / TEV / HFCT) matches the switchgear type and access. | Medium | Sensor method must suit the panel.
CR_029 | Must-have | FAULT_LOC_001 | Transmission line | Transmission line fault location is required | Offer a two-end, GPS-synchronised (traveling-wave or impedance) locator; confirm both line ends are instrumented. | High | Two-end sync required for accuracy.
CR_030 | Must-have | TR_BUSH_001 | Transformer bushing | Bushing condition monitoring is required | Confirm bushing tap availability and phase count (typically 3-phase) before selecting the monitor. | Medium | Requires bushing tap access.
CR_031 | Must-have | GIS_ARC_001 | GIS compartment | Arc-flash detection / localization is required | Offer fast (sub-millisecond) light/pressure arc-flash detection with a trip output. | High | Detection speed is safety-critical.
CR_032 | Must-have | WAMS_001 | Multi-substation grid | Wide-area monitoring (WAMS) is required | Requires PMUs plus a central PDC / WAMS platform; confirm both are in scope. | High | WAMS needs PMU + PDC.
CR_033 | Must-have | FMS_001 | Substation network server | Centralized fault management (FMS) is required | Requires a central server / master-station platform aggregating DFR/IEDs; confirm server tier. | High | FMS is a system, not a single device.
CR_034 | Must-have | TR_TEMP_001 | Power transformer | Winding / oil temperature monitoring is required | Confirm the sensing method (CT-based hot-spot vs fibre-optic direct) and number of windings monitored. | Medium | Method affects product choice.
CR_035 | Must-have | GEN_AIRGAP_001 | Hydro generator | Air-gap / rotor flux monitoring is required | Offer hydro air-gap monitoring; confirm number of poles/sensors and machine access. | Medium | Hydro-specific requirement.
CR_036 | Must-have | TR_DGA_001 | Oil-filled transformer | Multiple fault gases are explicitly required | Offer a multi-gas DGA monitor rather than a single-gas (H2-only) monitor. | Medium | Single-gas vs multi-gas selection.
CR_037 | Must-have | TR_PD_001 | Power transformer | Transformer partial discharge monitoring is required | Confirm the PD sensor type (UHF / HFCT / acoustic) and coupling method for the transformer. | Medium | Sensor/coupling method must be confirmed.
CR_MEA_01 | Selection | FMS_001 | Feeder / bay | FMS monitoring required on ALL feeders/bays ('Everywhere'). | Provide FMS on every feeder; minimum device IDM+ 9A/32D (3U). Increase analogue/digital channels as necessary. | Medium | TAQA/ADNOC MEA ruleset (Ruleset for TAQA ADNOC MEA Region - IP.xlsx); candidate — review before use.
CR_MEA_02 | Selection | PQ_CLASSA_001 | BS / BC / TX / Gen / 3rd-party feeder | PQM required on Bus Section (BS), Bus Coupler (BC), Transformer (TX) feeders, 3rd-party feeders and Gen feeders. | Provide PQM on these feeders using IDM+ 18A/64D or IDM+ 27A/96D (6U chassis). | Medium | TAQA/ADNOC MEA ruleset (Ruleset for TAQA ADNOC MEA Region - IP.xlsx); candidate — review before use.
CR_MEA_03 | Selection | PMU_001 | OHL / IC / Gen / 3rd-party feeder | PMU required on OHL feeders, IC feeder, Gen feeders and 3rd-party feeders; NOT on BC, NOT on BS. | Provide PMU on these feeders using IDM+ 36A/128D (6U). Do NOT place PMU on bus coupler / bus section feeders. | Medium | TAQA/ADNOC MEA ruleset (Ruleset for TAQA ADNOC MEA Region - IP.xlsx); candidate — review before use.
CR_MEA_04 | Selection | All | DAU chassis | TAQA-approved DAU chassis options. | Approved chassis: 3U 9A/32D (FMS/PQM/PMU); 6U 18A/64D (FMS/PQM or FMS/PMU). Comms = RJ45. Increase A/D as necessary. | Low | TAQA/ADNOC MEA ruleset (Ruleset for TAQA ADNOC MEA Region - IP.xlsx); candidate — review before use.
CR_MEA_05 | Quantity | All | Panel | Panel device capacity limit. | Max 4× 3U devices OR 2× 6U devices per panel; provide Option 1 & Option 2 when it affects panel count. | Medium | TAQA/ADNOC MEA ruleset (Ruleset for TAQA ADNOC MEA Region - IP.xlsx); candidate — review before use.
CR_MEA_06 | Quantity | PMU_001 | GPS timing | GPS master / antenna sizing. | 1 GPS Master per 12 DAU; 2 antennas incl. 100m cable, amplifier, mounting kit & surge arrestor. | Medium | TAQA/ADNOC MEA ruleset (Ruleset for TAQA ADNOC MEA Region - IP.xlsx); candidate — review before use.
CR_MEA_07 | Quantity | COMM_SCADA_001 | Ethernet switch | Monitoring-LAN port sizing. | 16-port Ethernet switch; allow 1 port per DAU; offer redundancy. | Low | TAQA/ADNOC MEA ruleset (Ruleset for TAQA ADNOC MEA Region - IP.xlsx); candidate — review before use.
CR_MEA_08 | Quantity | PMU_001 | EPG licence | EPG licence count per device. | 4 EPG licenses per device (FMS/PMU chassis); N/A for PQM 6U chassis. | Medium | TAQA/ADNOC MEA ruleset (Ruleset for TAQA ADNOC MEA Region - IP.xlsx); candidate — review before use.
CR_MEA_09 | Quantity | All | Test switch | Test switch allocation. | Provide test switches per device. | Low | TAQA/ADNOC MEA ruleset (Ruleset for TAQA ADNOC MEA Region - IP.xlsx); candidate — review before use.
CR_MEA_10 | Quantity | All | Annunciator | Annunciator allocation. | Provide one annunciator per panel. | Low | TAQA/ADNOC MEA ruleset (Ruleset for TAQA ADNOC MEA Region - IP.xlsx); candidate — review before use.
CR_MEA_11 | Bundle | COMM_SCADA_001 | LEV panel | FMS/PQM LEV panel standard contents. | Include: Industrial Rack Mounted PC, Trend Micro Antivirus, Trellix Whitelisting, Acronis Backup, iQ+ Software, 16 Port RJ45 4-port fiber L2 switch, 16 Port RJ45 4-port fiber L3 switch, Firewall, Printer, Annunciator. | Medium | TAQA/ADNOC MEA ruleset (Ruleset for TAQA ADNOC MEA Region - IP.xlsx); candidate — review before use.
CR_MEA_12 | Bundle | PMU_001;WAMS_001 | PDC panel | PDC panel standard contents. | Same as FMS/PQM LEV panel PLUS: Redundant Industrial Rack Mounted PC, eSPDC Software, total number of EPG Licenses, KVM. | Medium | TAQA/ADNOC MEA ruleset (Ruleset for TAQA ADNOC MEA Region - IP.xlsx); candidate — review before use.
CR_BAY_OHL | Selection | FMS_001;PMU_001 | OHL bay | Bay type = OHL (overhead line) feeder. | Configure FMS + PMU on OHL bays. Do NOT add PQM by default. | Medium | Engineer AE bay schedule (766481 BAHIA SASN) + TAQA MEA ruleset; candidate — review before use.
CR_BAY_TX | Selection | FMS_001;PQ_CLASSA_001 | Interbus / Power Transformer bay | Bay type = interbus transformer (IBT) or power transformer bay. | Configure FMS + PQM on transformer bays. | Medium | Engineer AE bay schedule (766481 BAHIA SASN) + TAQA MEA ruleset; candidate — review before use.
CR_BAY_BCBS | Selection | FMS_001;PQ_CLASSA_001 | Bus Coupler / Bus Section | Bay type = bus coupler (BC) or bus section (BS). | Configure FMS + PQM on BC/BS bays; do NOT place PMU on bus coupler / bus section. | Medium | Engineer AE bay schedule (766481 BAHIA SASN) + TAQA MEA ruleset; candidate — review before use.
CR_BAY_STATCOM | Selection | FMS_001;PQ_CLASSA_001;PMU_001 | STATCOM bay | Bay type = STATCOM. | Configure FMS + PQM + PMU on STATCOM bays. | Medium | Engineer AE bay schedule (766481 BAHIA SASN) + TAQA MEA ruleset; candidate — review before use.
CR_BAY_CAP | Selection | FMS_001;PQ_CLASSA_001;PMU_001 | Capacitor Bank bay | Bay type = capacitor bank. | Configure FMS + PQM + PMU on capacitor bank bays. | Medium | Engineer AE bay schedule (766481 BAHIA SASN) + TAQA MEA ruleset; candidate — review before use.
CR_BAY_IC | Selection | FMS_001;PMU_001 | Interconnector / Incomer bay | Bay type = interconnector (IC) or transformer incomer. | Configure FMS + PMU on IC / incomer bays (PMU per TAQA ruleset). | Medium | Engineer AE bay schedule (766481 BAHIA SASN) + TAQA MEA ruleset; candidate — review before use.
CR_BAY_FUTURE | Exclusion | All | Bay marked Future / Provision | Bay is marked 'Future' or 'Provision' in the bay schedule / SLD. | Exclude from BOQ quantity; list separately for engineer confirmation. | High | Engineer AE bay schedule (766481 BAHIA SASN) + TAQA MEA ruleset; candidate — review before use.
CR_BAY_SCOPE | Review | All | Monitored bay set | The actual monitored set may be a SOW-limited subset (only specific feeders, e.g. capacitor bank / cable feeders), NOT the whole substation. | Confirm the in-scope feeders/bays against the SOW before finalizing quantities; never assume every bay in the SLD is monitored. | High | Engineer AE bay schedule (766481 BAHIA SASN) + TAQA MEA ruleset; candidate — review before use.

## 11_SLD_Asset_Vocabulary
SLD Asset Vocabulary - Controlled Drawing Asset Types (record only)
Records the controlled SLD asset-type vocabulary the drawing extractor normalises to. RECORD ONLY - the pipeline still reads this vocabulary from code (_VALID_ASSET_TYPES in qualitrol_core/llm_extract.py and COUNT_FIELD_TO_ASSET_TYPE in qualitrol_core/constants.py), NOT from this sheet.
Asset Type | Category | Mapped Count Field(s) | Recognition Path | Notes
| Asset category | count_field(s) in constants.py used to size quantity | VLM = vision only; Text-layer + VLM = also detected on the text layer | Origin: core or expansion
Circuit Breaker | Primary plant | breaker_count | Text-layer + VLM | Original core vocabulary
Transformer | Primary plant | transformer_count | Text-layer + VLM | Original core vocabulary
GIS Bay | Switchgear / GIS | gis_bay_count | Text-layer + VLM | Original core vocabulary
Bus | Busbar | (via pcc_count / measurement_point_count) | Text-layer + VLM | Original core vocabulary
Feeder | Feeder / bay | feeder_count (also pcc_count / line_count) | Text-layer + VLM | Original core vocabulary
PCC | Connection point | pcc_count | Text-layer + VLM | Original core vocabulary
Generator | Rotating machine | generator_count | VLM | Original core vocabulary
Motor | Rotating machine | motor_count | VLM | Original core vocabulary
Switchgear Panel | Switchgear | panel_count | VLM | Original core vocabulary
PD Sensor | Sensor | sensor_count | Text-layer + VLM | Original core vocabulary
Sensor | Sensor | sensor_count / accessory_count | VLM | Original core vocabulary
Bushing | Transformer accessory | bushing_count | VLM | Original core vocabulary
Channel | Recorder channel | channel_count | VLM | Original core vocabulary
Measurement Point | Measurement | measurement_point_count | VLM | Original core vocabulary
Reactor | Primary plant | reactor_count | VLM | Added in 2026-07 expansion
Transmission Line | Line | transmission_line_count / line_count | VLM | Added in 2026-07 expansion
Cable | Line / cable | cable_count | VLM | Added in 2026-07 expansion
Surge Arrester | Primary plant | surge_arrester_count | VLM | Added in 2026-07 expansion
Instrument Transformer | Instrument transformer (CT/VT) | instrument_transformer_count | VLM | Added in 2026-07 expansion
Tap Changer | Transformer accessory (OLTC) | tap_changer_count | VLM | Added in 2026-07 expansion
Capacitor Bank | Reactive compensation | capacitor_bank_count | VLM | Added in 2026-07 expansion
Cabinet | Enclosure / environmental | cabinet_count | VLM | Added in 2026-07 expansion

## 17_Missing_Info_Questions (hidden)
Missing Information and Clarification Questions
Use this sheet to prevent the AI from guessing. Missing information should generate customer or engineer clarification questions.
Project ID | Missing Information Item | Related Scenario ID | Why It Matters | Suggested Customer / Engineer Question | Priority | Owner | Status | Notes
Header anchor only; value ignored by the pipeline. |  | Scenario (sheet 03) this question relates to; used to pick templates. | Explanation copied into project output. | Question text copied into project output. | High/Medium/Low; used to sort questions. | Responsible role; copied into output. | Ignored by loader (forced to 'Open'). | Human note; not used by the pipeline.
| Transformer oil type | TR_DGA_001 | Required to confirm DGA applicability and compatibility. | Please confirm whether the transformer uses mineral oil, ester oil, or another insulation fluid. | High | Sales / Product Engineer | Open
| Number of monitored transformers | TR_DGA_001; TR_TEMP_001 | Required for BOQ quantity. | Please confirm how many transformers are included in the monitoring scope. | High | Sales / Customer | Open
| Circuit breaker count | BRK_HEALTH_001 | Required for breaker monitor quantity. | Please provide the latest SLD or breaker equipment list. | High | Sales / Customer | Open
| GIS bay layout | GIS_PD_001 | Required for PD sensor placement and quantity. | Please provide GIS layout, bay list, or monitoring zone definition. | High | Product Engineer | Open
| Power quality class | PQ_CLASSA_001 | Determines whether Class A product capability is mandatory. | Please confirm whether Class A power quality compliance is required. | Medium | Sales / Customer | Open
| Communication protocol | COMM_SCADA_001 | Required for integration and gateway selection. | Please confirm required protocol: Modbus, DNP3, IEC 61850, IEC 60870, or other. | Medium | Customer IT / SCADA | Open
| Ambient temperature and humidity | CAB_ENV_001 | Required for enclosure and environmental suitability. | Please confirm site operating temperature and humidity range. | Medium | Customer / Engineer | Open
| Recorder channel list | DFR_DDR_001; PQ_CLASSA_001 | Required for DFR/PQ configuration and quantity. | Please provide voltage/current channel list and monitored feeders/buses. | High | Protection Engineer | Open